## Hmi Tags (1)
Name | Path | Connection | PLC tag | DataType | HMI DataType | Length | Coding | Access Method | Address | Start value | Quality Code | Persistency | Substitute value | Tag value [en-US] | Update Mode | Comment [en-US] | Raw data mode | R_ID | Limit Upper 2 Type | Limit Upper 2 | Limit Lower 2 Type | Limit Lower 2 | Linear scaling | End value PLC | Start value PLC | End value HMI | Start value HMI | Synchronization
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_350(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11."Events byte_350_365_b0_1".event_350 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1224.0 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_351(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11."Events byte_350_365_b0_1".event_351 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1224.1 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_352(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11."Events byte_350_365_b0_1".event_352 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1224.2 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_353(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11."Events byte_350_365_b0_1".event_353 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1224.3 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_354(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11."Events byte_350_365_b0_1".event_354 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1224.4 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_355(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11."Events byte_350_365_b0_1".event_355 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1224.5 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_356(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11."Events byte_350_365_b0_1".event_356 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1224.6 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_357(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11."Events byte_350_365_b0_1".event_357 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1224.7 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_358(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11."Events byte_350_365_b0_1".event_358 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1225.0 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_359(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11."Events byte_350_365_b0_1".event_359 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1225.1 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_360(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11."Events byte_350_365_b0_1".event_360 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1225.2 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_361(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11."Events byte_350_365_b0_1".event_361 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1225.3 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_362(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11."Events byte_350_365_b0_1".event_362 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1225.4 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_363(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11."Events byte_350_365_b0_1".event_363 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1225.5 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_364(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11."Events byte_350_365_b0_1".event_364 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1225.6 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_365(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11."Events byte_350_365_b0_1".event_365 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1225.7 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_Change_work(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Control_Byte_b2_3.Change_work | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1226.0 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_Res(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Control_Byte_b2_3.Res | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1226.1 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_Set_time(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Control_Byte_b2_3.Set_time | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1226.2 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_Cb3(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Control_Byte_b2_3.Cb3 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1226.3 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_Cb4(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Control_Byte_b2_3.Cb4 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1226.4 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_Cb5(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Control_Byte_b2_3.Cb5 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1226.5 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_Cb6(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Control_Byte_b2_3.Cb6 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1226.6 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_Cb7(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Control_Byte_b2_3.Cb7 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1226.7 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_local(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Control_Byte_b2_3.local | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1227.0 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_remote(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Control_Byte_b2_3.remote | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1227.1 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_SCADA(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Control_Byte_b2_3.SCADA | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1227.2 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_test_local(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Control_Byte_b2_3.test_local | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1227.3 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_test_remote(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Control_Byte_b2_3.test_remote | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1227.4 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_NM5(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Control_Byte_b2_3.NM5 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1227.5 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_NM6(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Control_Byte_b2_3.NM6 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1227.6 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_NM7(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Control_Byte_b2_3.NM7 | Bool | Bool | 1 | Binary | Absolute access | %DB1.DBX1227.7 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Time_set_b4_11_month(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Time_set_b4_11.month | Byte | USInt | 1 | Binary | Absolute access | %DB1.DBB1228 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Time_set_b4_11_year(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Time_set_b4_11.year | Byte | USInt | 1 | Binary | Absolute access | %DB1.DBB1229 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Time_set_b4_11_hour(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Time_set_b4_11.hour | Byte | USInt | 1 | Binary | Absolute access | %DB1.DBB1230 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Time_set_b4_11_day(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Time_set_b4_11.day | Byte | USInt | 1 | Binary | Absolute access | %DB1.DBB1231 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Time_set_b4_11_second(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Time_set_b4_11.second | Byte | USInt | 1 | Binary | Absolute access | %DB1.DBB1232 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Time_set_b4_11_minute(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Time_set_b4_11.minute | Byte | USInt | 1 | Binary | Absolute access | %DB1.DBB1233 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Time_set_b4_11_millisecondhigh_Byte(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Time_set_b4_11."millisecond high_Byte" | Byte | USInt | 1 | Binary | Absolute access | %DB1.DBB1234 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Time_set_b4_11_millisecondlow_Byte(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_1_b0_11.Time_set_b4_11."millisecond low_Byte" | Byte | USInt | 1 | Binary | Absolute access | %DB1.DBB1235 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_30_b12_15_instr_No_1_b5(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_30_b12_15.instr_No_1_b5 | Byte | USInt | 1 | Binary | Absolute access | %DB1.DBB1236 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_30_b12_15_instr_No_2_b6(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_30_b12_15.instr_No_2_b6 | Byte | USInt | 1 | Binary | Absolute access | %DB1.DBB1237 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_30_b12_15_Data_val_1_b7(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_30_b12_15.Data_val_1_b7 | Byte | USInt | 1 | Binary | Absolute access | %DB1.DBB1238 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_30_b12_15_Data_val_2_b8(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Out.module_30_b12_15.Data_val_2_b8 | Byte | USInt | 1 | Binary | Absolute access | %DB1.DBB1239 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_FR_b14_15(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_FR_b14_15 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1240 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_U1_b16_17(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_U1_b16_17 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1244 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_U2_b18_19(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_U2_b18_19 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1248 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_U3_b20_21(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_U3_b20_21 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1252 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_U12_b22_23(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_U12_b22_23 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1256 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_U13_b24_25(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_U13_b24_25 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1260 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_U23_b26_27(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_U23_b26_27 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1264 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_UAvr_b28_29(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_UAvr_b28_29 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1268 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS1_FR_b31_32(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.BUS1_FR_b31_32 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1272 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS1_U1_b32_33(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.BUS1_U1_b32_33 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1276 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS1_U2_b34_35(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.BUS1_U2_b34_35 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1280 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS1_U3_b36_37(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.BUS1_U3_b36_37 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1284 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS1_U12_b38_39(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.BUS1_U12_b38_39 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1288 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS1_U13_b40_41(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.BUS1_U13_b40_41 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1292 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS1_U23_b42_43(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.BUS1_U23_b42_43 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1296 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS1_UAvr_b44_45(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.BUS1_UAvr_b44_45 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1300 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS2_FR_b46_47(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.BUS2_FR_b46_47 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1304 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS2_U1_b48_49(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.BUS2_U1_b48_49 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1308 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS2_U2_b50_51(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.BUS2_U2_b50_51 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1312 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS2_U3_b52_53(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.BUS2_U3_b52_53 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1316 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS2_U12_b54_55(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.BUS2_U12_b54_55 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1320 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS2_U13_b56_57(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.BUS2_U13_b56_57 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1324 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS2_U23_b58_59(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.BUS2_U23_b58_59 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1328 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS2_UAvr_b60_61(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.BUS2_UAvr_b60_61 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1332 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_I1_b62_63(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_I1_b62_63 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1336 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_I2_b64_65(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_I2_b64_65 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1340 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_I3_b65_67(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_I3_b65_67 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1344 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_IAvr_b68_69(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_IAvr_b68_69 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1348 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_P(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_P | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1352 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_Q(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_Q | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1356 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_S(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_S | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1360 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_PF(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_PF | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1364 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_PL1(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_PL1 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1368 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_PL2(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_PL2 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1372 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_PL3(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_PL3 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1376 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_QL1(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_QL1 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1380 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_QL2(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_QL2 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1384 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_QL3(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_QL3 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1388 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_PFL1(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_PFL1 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1392 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_PFL2(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_PFL2 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1396 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_PFL3(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Filtered.FDR_PFL3 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1400 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_7_b14_29_Fc_FDR_FR_b14_15(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_7_b14_29.Fc_FDR_FR_b14_15 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1404 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_7_b14_29_Fc_FDR_U1_b16_17(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_7_b14_29.Fc_FDR_U1_b16_17 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1408 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_7_b14_29_Fc_FDR_U2_b18_19(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_7_b14_29.Fc_FDR_U2_b18_19 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1412 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_7_b14_29_Fc_FDR_U3_b20_21(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_7_b14_29.Fc_FDR_U3_b20_21 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1416 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_7_b14_29_Fc_FDR_U12_b22_23(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_7_b14_29.Fc_FDR_U12_b22_23 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1420 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_7_b14_29_Fc_FDR_U13_b24_25(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_7_b14_29.Fc_FDR_U13_b24_25 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1424 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_7_b14_29_Fc_FDR_U23_b26_27(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_7_b14_29.Fc_FDR_U23_b26_27 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1428 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_7_b14_29_Fc_FDR_UAvr_b28_29(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_7_b14_29.Fc_FDR_UAvr_b28_29 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1432 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_830_45_Fc_BUS1_FR_b31_32(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_830_45.Fc_BUS1_FR_b31_32 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1436 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_830_45_Fc_BUS1_U1_b32_33(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_830_45.Fc_BUS1_U1_b32_33 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1440 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_830_45_Fc_BUS1_U2_b34_35(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_830_45.Fc_BUS1_U2_b34_35 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1444 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_830_45_Fc_BUS1_U3_b36_37(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_830_45.Fc_BUS1_U3_b36_37 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1448 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_830_45_Fc_BUS1_U12_b38_39(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_830_45.Fc_BUS1_U12_b38_39 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1452 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_830_45_Fc_BUS1_U13_b40_41(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_830_45.Fc_BUS1_U13_b40_41 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1456 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_830_45_Fc_BUS1_U23_b42_43(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_830_45.Fc_BUS1_U23_b42_43 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1460 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_830_45_Fc_BUS1_UAvr_b44_45(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_830_45.Fc_BUS1_UAvr_b44_45 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1464 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_9_b46_61_Fc_BUS2_FR_b46_47(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_9_b46_61.Fc_BUS2_FR_b46_47 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1468 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_9_b46_61_Fc_BUS2_U1_b48_49(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_9_b46_61.Fc_BUS2_U1_b48_49 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1472 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_9_b46_61_Fc_BUS2_U2_b50_51(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_9_b46_61.Fc_BUS2_U2_b50_51 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1476 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_9_b46_61_Fc_BUS2_U3_b52_53(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_9_b46_61.Fc_BUS2_U3_b52_53 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1480 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_9_b46_61_Fc_BUS2_U12_b54_55(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_9_b46_61.Fc_BUS2_U12_b54_55 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1484 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_9_b46_61_Fc_BUS2_U13_b56_57(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_9_b46_61.Fc_BUS2_U13_b56_57 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1488 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_9_b46_61_Fc_BUS2_U23_b58_59(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_9_b46_61.Fc_BUS2_U23_b58_59 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1492 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_9_b46_61_Fc_BUS2_UAvr_b60_61(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_9_b46_61.Fc_BUS2_UAvr_b60_61 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1496 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_10_b62_69_Fc_FDR_I1_b62_63(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_10_b62_69.Fc_FDR_I1_b62_63 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1500 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_10_b62_69_Fc_FDR_I2_b64_65(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_10_b62_69.Fc_FDR_I2_b64_65 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1504 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_10_b62_69_Fc_FDR_I3_b65_67(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_10_b62_69.Fc_FDR_I3_b65_67 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1508 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_10_b62_69_Fc_FDR_IAvr_b68_69(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_10_b62_69.Fc_FDR_IAvr_b68_69 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1512 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_12_b70_77_Fc_FDR_P_b70_71(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_12_b70_77.Fc_FDR_P_b70_71 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1516 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_12_b70_77_Fc_FDR_Q_b72_73(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_12_b70_77.Fc_FDR_Q_b72_73 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1520 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_12_b70_77_Fc_FDR_S_b74_75(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_12_b70_77.Fc_FDR_S_b74_75 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1524 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_12_b70_77_Fc_FDR_PF_b76_77(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_12_b70_77.Fc_FDR_PF_b76_77 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1528 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_13_b78_83_Fc_FDR_PL1_b78_79(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_13_b78_83.Fc_FDR_PL1_b78_79 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1532 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_13_b78_83_Fc_FDR_PL2_b80_81(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_13_b78_83.Fc_FDR_PL2_b80_81 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1536 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_13_b78_83_Fc_FDR_PL3_b82_83(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_13_b78_83.Fc_FDR_PL3_b82_83 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1540 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_14_b84_89_Fc_FDR_QL1_b84_85(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_14_b84_89.Fc_FDR_QL1_b84_85 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1544 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_14_b84_89_Fc_FDR_QL2_b86_87(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_14_b84_89.Fc_FDR_QL2_b86_87 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1548 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_14_b84_89_Fc_FDR_QL3_b88_89(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_14_b84_89.Fc_FDR_QL3_b88_89 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1552 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_15_b90_95_Fc_FDR_PFL1_b90_91(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_15_b90_95.Fc_FDR_PFL1_b90_91 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1556 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_15_b90_95_Fc_FDR_PFL2_b92_93(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_15_b90_95.Fc_FDR_PFL2_b92_93 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1560 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_15_b90_95_Fc_FDR_PFL3_b94_95(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_15_b90_95.Fc_FDR_PFL3_b94_95 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1564 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_18_b96_111_Fc_P_activ_b96_99(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_18_b96_111.Fc_P_activ_b96_99 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1568 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_18_b96_111_Fc_P_obr_b100_103(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_18_b96_111.Fc_P_obr_b100_103 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1572 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_18_b96_111_Fc_P_emk_reakt_b104_107(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_18_b96_111.Fc_P_emk_reakt_b104_107 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1576 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_18_b96_111_Fc_P_ind_reakt_b108_111(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_18_b96_111.Fc_P_ind_reakt_b108_111 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1580 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_16_b112_119_Fc_Io1_b112_113(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_16_b112_119.Fc_Io1_b112_113 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1584 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_16_b112_119_Fc_Uo1_b114_115(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_16_b112_119.Fc_Uo1_b114_115 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1588 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_16_b112_119_Fc_Po1_b116_117(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_16_b112_119.Fc_Po1_b116_117 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1592 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_16_b112_119_Fc_Qo1_b118_119(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_16_b112_119.Fc_Qo1_b118_119 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1596 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_25_b120_129_Fc_Alarm1_b120_121(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_25_b120_129.Fc_Alarm1_b120_121 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1600 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_25_b120_129_Fc_Alarm2_b122_123(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_25_b120_129.Fc_Alarm2_b122_123 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1604 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_25_b120_129_Fc_Alarm3_b124_125(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_25_b120_129.Fc_Alarm3_b124_125 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1608 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_25_b120_129_Fc_Alarm4_b126_127(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_25_b120_129.Fc_Alarm4_b126_127 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1612 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_25_b120_129_Fc_Alarm5_b128_129(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_25_b120_129.Fc_Alarm5_b128_129 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1616 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_Gen_number_b130_131(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_31_b130_155.Fc_PM_Gen_number_b130_131 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1620 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_BCG_prstatus_b132_133(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_31_b130_155.Fc_PM_BCG_prstatus_b132_133 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1624 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_BCG_ownstatus_b134_135(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_31_b130_155.Fc_PM_BCG_ownstatus_b134_135 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1628 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_BCG_netstatus_b136_137(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_31_b130_155.Fc_PM_BCG_netstatus_b136_137 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1632 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_8_9_b138_139(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_31_b130_155.Fc_PM_8_9_b138_139 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1636 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_10_11_b140_141(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_31_b130_155.Fc_PM_10_11_b140_141 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1640 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_12_13_b142_143(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_31_b130_155.Fc_PM_12_13_b142_143 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1644 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_14_15_b144_145(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_31_b130_155.Fc_PM_14_15_b144_145 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1648 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_16_17_b146_147(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_31_b130_155.Fc_PM_16_17_b146_147 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1652 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_18_19_b148_149(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_31_b130_155.Fc_PM_18_19_b148_149 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1656 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_20_21_b150_151(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_31_b130_155.Fc_PM_20_21_b150_151 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1660 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_asym_load_point_b152_153(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_31_b130_155.Fc_PM_asym_load_point_b152_153 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1664 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_asym_power_factor_b151_155(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_31_b130_155.Fc_PM_asym_power_factor_b151_155 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1668 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_32_b156_173_Fc_P_kw_b156_157(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_32_b156_173.Fc_P_kw_b156_157 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1672 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_32_b156_173_Fc_P_ps_b158_159(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_32_b156_173.Fc_P_ps_b158_159 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1676 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_32_b156_173_Fc_F_I_amp_b160_161(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_32_b156_173.Fc_F_I_amp_b160_161 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1680 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_32_b156_173_Fc_F_I_ps_b162_163(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_32_b156_173.Fc_F_I_ps_b162_163 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1684 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_32_b156_173_Fc_F_U_b164_165(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_32_b156_173.Fc_F_U_b164_165 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1688 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_32_b156_173_Fc_F_freg_b166_167(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_32_b156_173.Fc_F_freg_b166_167 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1692 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_32_b156_173_Fc_F_cosf_b168_169(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_32_b156_173.Fc_F_cosf_b168_169 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1696 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_32_b156_173_Fc_B1_U_b170_171(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_32_b156_173.Fc_B1_U_b170_171 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1700 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_32_b156_173_Fc_B1_freg1_b172_173(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_32_b156_173.Fc_B1_freg1_b172_173 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1704 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_33_b174_189_Fc_RPM_b174_175(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_33_b174_189.Fc_RPM_b174_175 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1708 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_33_b174_189_Fc_BR1_ON_cycles_b176_177(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_33_b174_189.Fc_BR1_ON_cycles_b176_177 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1712 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_33_b174_189_Fc_BR2_ON_cycles_b178_179(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_33_b174_189.Fc_BR2_ON_cycles_b178_179 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1716 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_33_b174_189_Fc_BR3_ON_cycles_b180_181(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_33_b174_189.Fc_BR3_ON_cycles_b180_181 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1720 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_33_b174_189_Fc_Start_counter_b182_183(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_33_b174_189.Fc_Start_counter_b182_183 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1724 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_33_b174_189_Fc_DP_MD33_R1_b184_185(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_33_b174_189.Fc_DP_MD33_R1_b184_185 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1728 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_33_b174_189_Fc_DP_MD33_R2_b186_187(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_33_b174_189.Fc_DP_MD33_R2_b186_187 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1732 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_33_b174_189_Fc_DP_MD33_R3_b188_189(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.Factor.modul_33_b174_189.Fc_DP_MD33_R3_b188_189 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1736 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_7_b14_29_Fc_FDR_FR_b14_15(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_7_b14_29.Fc_FDR_FR_b14_15 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1740 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_7_b14_29_Fc_FDR_U1_b16_17(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_7_b14_29.Fc_FDR_U1_b16_17 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1744 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_7_b14_29_Fc_FDR_U2_b18_19(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_7_b14_29.Fc_FDR_U2_b18_19 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1748 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_7_b14_29_Fc_FDR_U3_b20_21(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_7_b14_29.Fc_FDR_U3_b20_21 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1752 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_7_b14_29_Fc_FDR_U12_b22_23(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_7_b14_29.Fc_FDR_U12_b22_23 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1756 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_7_b14_29_Fc_FDR_U13_b24_25(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_7_b14_29.Fc_FDR_U13_b24_25 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1760 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_7_b14_29_Fc_FDR_U23_b26_27(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_7_b14_29.Fc_FDR_U23_b26_27 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1764 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_7_b14_29_Fc_FDR_UAvr_b28_29(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_7_b14_29.Fc_FDR_UAvr_b28_29 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1768 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_830_45_Fc_BUS1_FR_b31_32(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_830_45.Fc_BUS1_FR_b31_32 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1772 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_830_45_Fc_BUS1_U1_b32_33(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_830_45.Fc_BUS1_U1_b32_33 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1776 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_830_45_Fc_BUS1_U2_b34_35(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_830_45.Fc_BUS1_U2_b34_35 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1780 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_830_45_Fc_BUS1_U3_b36_37(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_830_45.Fc_BUS1_U3_b36_37 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1784 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_830_45_Fc_BUS1_U12_b38_39(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_830_45.Fc_BUS1_U12_b38_39 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1788 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_830_45_Fc_BUS1_U13_b40_41(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_830_45.Fc_BUS1_U13_b40_41 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1792 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_830_45_Fc_BUS1_U23_b42_43(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_830_45.Fc_BUS1_U23_b42_43 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1796 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_830_45_Fc_BUS1_UAvr_b44_45(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_830_45.Fc_BUS1_UAvr_b44_45 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1800 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_9_b46_61_Fc_BUS2_FR_b46_47(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_9_b46_61.Fc_BUS2_FR_b46_47 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1804 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_9_b46_61_Fc_BUS2_U1_b48_49(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_9_b46_61.Fc_BUS2_U1_b48_49 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1808 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_9_b46_61_Fc_BUS2_U2_b50_51(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_9_b46_61.Fc_BUS2_U2_b50_51 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1812 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_9_b46_61_Fc_BUS2_U3_b52_53(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_9_b46_61.Fc_BUS2_U3_b52_53 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1816 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_9_b46_61_Fc_BUS2_U12_b54_55(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_9_b46_61.Fc_BUS2_U12_b54_55 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1820 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_9_b46_61_Fc_BUS2_U13_b56_57(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_9_b46_61.Fc_BUS2_U13_b56_57 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1824 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_9_b46_61_Fc_BUS2_U23_b58_59(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_9_b46_61.Fc_BUS2_U23_b58_59 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1828 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_9_b46_61_Fc_BUS2_UAvr_b60_61(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_9_b46_61.Fc_BUS2_UAvr_b60_61 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1832 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_10_b62_69_Fc_FDR_I1_b62_63(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_10_b62_69.Fc_FDR_I1_b62_63 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1836 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_10_b62_69_Fc_FDR_I2_b64_65(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_10_b62_69.Fc_FDR_I2_b64_65 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1840 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_10_b62_69_Fc_FDR_I3_b65_67(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_10_b62_69.Fc_FDR_I3_b65_67 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1844 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_10_b62_69_Fc_FDR_IAvr_b68_69(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_10_b62_69.Fc_FDR_IAvr_b68_69 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1848 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_12_b70_77_Fc_FDR_P_b70_71(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_12_b70_77.Fc_FDR_P_b70_71 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1852 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_12_b70_77_Fc_FDR_Q_b72_73(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_12_b70_77.Fc_FDR_Q_b72_73 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1856 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_12_b70_77_Fc_FDR_S_b74_75(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_12_b70_77.Fc_FDR_S_b74_75 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1860 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_12_b70_77_Fc_FDR_PF_b76_77(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_12_b70_77.Fc_FDR_PF_b76_77 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1864 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_13_b78_83_Fc_FDR_PL1_b78_79(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_13_b78_83.Fc_FDR_PL1_b78_79 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1868 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_13_b78_83_Fc_FDR_PL2_b80_81(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_13_b78_83.Fc_FDR_PL2_b80_81 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1872 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_13_b78_83_Fc_FDR_PL3_b82_83(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_13_b78_83.Fc_FDR_PL3_b82_83 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1876 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_14_b84_89_Fc_FDR_QL1_b84_85(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_14_b84_89.Fc_FDR_QL1_b84_85 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1880 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_14_b84_89_Fc_FDR_QL2_b86_87(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_14_b84_89.Fc_FDR_QL2_b86_87 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1884 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_14_b84_89_Fc_FDR_QL3_b88_89(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_14_b84_89.Fc_FDR_QL3_b88_89 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1888 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_15_b90_95_Fc_FDR_PFL1_b90_91(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_15_b90_95.Fc_FDR_PFL1_b90_91 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1892 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_15_b90_95_Fc_FDR_PFL2_b92_93(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_15_b90_95.Fc_FDR_PFL2_b92_93 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1896 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_15_b90_95_Fc_FDR_PFL3_b94_95(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_15_b90_95.Fc_FDR_PFL3_b94_95 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1900 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_18_b96_111_Fc_P_activ_b96_99(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_18_b96_111.Fc_P_activ_b96_99 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1904 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_18_b96_111_Fc_P_obr_b100_103(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_18_b96_111.Fc_P_obr_b100_103 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1908 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_18_b96_111_Fc_P_emk_reakt_b104_107(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_18_b96_111.Fc_P_emk_reakt_b104_107 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1912 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_18_b96_111_Fc_P_ind_reakt_b108_111(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_18_b96_111.Fc_P_ind_reakt_b108_111 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1916 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_16_b112_119_Fc_Io1_b112_113(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_16_b112_119.Fc_Io1_b112_113 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1920 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_16_b112_119_Fc_Uo1_b114_115(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_16_b112_119.Fc_Uo1_b114_115 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1924 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_16_b112_119_Fc_Po1_b116_117(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_16_b112_119.Fc_Po1_b116_117 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1928 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_16_b112_119_Fc_Qo1_b118_119(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_16_b112_119.Fc_Qo1_b118_119 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1932 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_25_b120_129_Fc_Alarm1_b120_121(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_25_b120_129.Fc_Alarm1_b120_121 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1936 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_25_b120_129_Fc_Alarm2_b122_123(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_25_b120_129.Fc_Alarm2_b122_123 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1940 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_25_b120_129_Fc_Alarm3_b124_125(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_25_b120_129.Fc_Alarm3_b124_125 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1944 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_25_b120_129_Fc_Alarm4_b126_127(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_25_b120_129.Fc_Alarm4_b126_127 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1948 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_25_b120_129_Fc_Alarm5_b128_129(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_25_b120_129.Fc_Alarm5_b128_129 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1952 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_Gen_number_b130_131(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_31_b130_155.Fc_PM_Gen_number_b130_131 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1956 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_BCG_prstatus_b132_133(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_31_b130_155.Fc_PM_BCG_prstatus_b132_133 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1960 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_BCG_ownstatus_b134_135(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_31_b130_155.Fc_PM_BCG_ownstatus_b134_135 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1964 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_BCG_netstatus_b136_137(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_31_b130_155.Fc_PM_BCG_netstatus_b136_137 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1968 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_8_9_b138_139(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_31_b130_155.Fc_PM_8_9_b138_139 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1972 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_10_11_b140_141(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_31_b130_155.Fc_PM_10_11_b140_141 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1976 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_12_13_b142_143(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_31_b130_155.Fc_PM_12_13_b142_143 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1980 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_14_15_b144_145(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_31_b130_155.Fc_PM_14_15_b144_145 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1984 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_16_17_b146_147(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_31_b130_155.Fc_PM_16_17_b146_147 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1988 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_18_19_b148_149(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_31_b130_155.Fc_PM_18_19_b148_149 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1992 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_20_21_b150_151(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_31_b130_155.Fc_PM_20_21_b150_151 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD1996 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_asym_load_point_b152_153(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_31_b130_155.Fc_PM_asym_load_point_b152_153 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2000 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_asym_power_factor_b151_155(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_31_b130_155.Fc_PM_asym_power_factor_b151_155 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2004 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_32_b156_173_Fc_P_kw_b156_157(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_32_b156_173.Fc_P_kw_b156_157 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2008 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_32_b156_173_Fc_P_ps_b158_159(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_32_b156_173.Fc_P_ps_b158_159 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2012 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_32_b156_173_Fc_F_I_amp_b160_161(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_32_b156_173.Fc_F_I_amp_b160_161 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2016 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_32_b156_173_Fc_F_I_ps_b162_163(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_32_b156_173.Fc_F_I_ps_b162_163 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2020 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_32_b156_173_Fc_F_U_b164_165(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_32_b156_173.Fc_F_U_b164_165 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2024 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_32_b156_173_Fc_F_freg_b166_167(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_32_b156_173.Fc_F_freg_b166_167 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2028 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_32_b156_173_Fc_F_cosf_b168_169(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_32_b156_173.Fc_F_cosf_b168_169 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2032 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_32_b156_173_Fc_B1_U_b170_171(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_32_b156_173.Fc_B1_U_b170_171 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2036 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_32_b156_173_Fc_B1_freg1_b172_173(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_32_b156_173.Fc_B1_freg1_b172_173 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2040 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_33_b174_189_Fc_RPM_b174_175(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_33_b174_189.Fc_RPM_b174_175 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2044 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_33_b174_189_Fc_BR1_ON_cycles_b176_177(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_33_b174_189.Fc_BR1_ON_cycles_b176_177 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2048 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_33_b174_189_Fc_BR2_ON_cycles_b178_179(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_33_b174_189.Fc_BR2_ON_cycles_b178_179 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2052 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_33_b174_189_Fc_BR3_ON_cycles_b180_181(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_33_b174_189.Fc_BR3_ON_cycles_b180_181 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2056 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_33_b174_189_Fc_Start_counter_b182_183(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_33_b174_189.Fc_Start_counter_b182_183 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2060 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_33_b174_189_Fc_DP_MD33_R1_b184_185(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_33_b174_189.Fc_DP_MD33_R1_b184_185 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2064 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_33_b174_189_Fc_DP_MD33_R2_b186_187(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_33_b174_189.Fc_DP_MD33_R2_b186_187 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2068 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_33_b174_189_Fc_DP_MD33_R3_b188_189(1) | symap_3 | HMI_Connection_2 | Read_write_Symap_Db.Devices[2].Wincc.K_Filter.modul_33_b174_189.Fc_DP_MD33_R3_b188_189 | Real | Real | 4 | IEEE754 | Absolute access | %DB1.DBD2072 | <No Value> | False | False | <No Value> | <No Value> | Client/Server wide | <No Value> | <No Value> | <No Value> | None | <No Value> | None | <No Value> | False | 10 | 0 | 100 | 0 | False

## Hmi Tags
Name | DataType
b0_1_event_350 | Bool | "b0_1_event_350" : Bool;
b0_1_event_351 | Bool | "b0_1_event_351" : Bool;
b0_1_event_352 | Bool | "b0_1_event_352" : Bool;
b0_1_event_353 | Bool | "b0_1_event_353" : Bool;
b0_1_event_354 | Bool | "b0_1_event_354" : Bool;
b0_1_event_355 | Bool | "b0_1_event_355" : Bool;
b0_1_event_356 | Bool | "b0_1_event_356" : Bool;
b0_1_event_357 | Bool | "b0_1_event_357" : Bool;
b0_1_event_358 | Bool | "b0_1_event_358" : Bool;
b0_1_event_359 | Bool | "b0_1_event_359" : Bool;
b0_1_event_360 | Bool | "b0_1_event_360" : Bool;
b0_1_event_361 | Bool | "b0_1_event_361" : Bool;
b0_1_event_362 | Bool | "b0_1_event_362" : Bool;
b0_1_event_363 | Bool | "b0_1_event_363" : Bool;
b0_1_event_364 | Bool | "b0_1_event_364" : Bool;
b0_1_event_365 | Bool | "b0_1_event_365" : Bool;
Change_work | Bool | "Change_work" : Bool;
Res | Bool | "Res" : Bool;
Set_time | Bool | "Set_time" : Bool;
Cb3 | Bool | "Cb3" : Bool;
Cb4 | Bool | "Cb4" : Bool;
Cb5 | Bool | "Cb5" : Bool;
Cb6 | Bool | "Cb6" : Bool;
Cb7 | Bool | "Cb7" : Bool;
local | Bool | "local" : Bool;
remote | Bool | "remote" : Bool;
SCADA | Bool | "SCADA" : Bool;
test_local | Bool | "test_local" : Bool;
test_remote | Bool | "test_remote" : Bool;
NM5 | Bool | "NM5" : Bool;
NM6 | Bool | "NM6" : Bool;
NM7 | Bool | "NM7" : Bool;
Time_set_b4_11_month | Byte | "Time_set_b4_11_month" : Byte;
Time_set_b4_11_year | Byte | "Time_set_b4_11_year" : Byte;
Time_set_b4_11_hour | Byte | "Time_set_b4_11_hour" : Byte;
Time_set_b4_11_day | Byte | "Time_set_b4_11_day" : Byte;
Time_set_b4_11_second | Byte | "Time_set_b4_11_second" : Byte;
Time_set_b4_11_minute | Byte | "Time_set_b4_11_minute" : Byte;
Time_set_b4_11_millisecondhigh_Byte | Byte | "Time_set_b4_11_millisecondhigh_Byte" : Byte;
Time_set_b4_11_millisecondlow_Byte | Byte | "Time_set_b4_11_millisecondlow_Byte" : Byte;
_instr_No_1_b5 | Byte | "_instr_No_1_b5" : Byte;
_instr_No_2_b6 | Byte | "_instr_No_2_b6" : Byte;
_Data_val_1_b7 | Byte | "_Data_val_1_b7" : Byte;
_Data_val_2_b8 | Byte | "_Data_val_2_b8" : Byte;
Fil_FDR_FR_b14_15 | Real | "Fil_FDR_FR_b14_15" : Real;
Fil_FDR_U1_b16_17 | Real | "Fil_FDR_U1_b16_17" : Real;
Fil_FDR_U2_b18_19 | Real | "Fil_FDR_U2_b18_19" : Real;
Fil_FDR_U3_b20_21 | Real | "Fil_FDR_U3_b20_21" : Real;
Fil_FDR_U12_b22_23 | Real | "Fil_FDR_U12_b22_23" : Real;
Fil_FDR_U13_b24_25 | Real | "Fil_FDR_U13_b24_25" : Real;
Fil_FDR_U23_b26_27 | Real | "Fil_FDR_U23_b26_27" : Real;
Fil_FDR_UAvr_b28_29 | Real | "Fil_FDR_UAvr_b28_29" : Real;
Fil_BUS1_FR_b31_32 | Real | "Fil_BUS1_FR_b31_32" : Real;
Fil_BUS1_U1_b32_33 | Real | "Fil_BUS1_U1_b32_33" : Real;
Fil_BUS1_U2_b34_35 | Real | "Fil_BUS1_U2_b34_35" : Real;
Fil_BUS1_U3_b36_37 | Real | "Fil_BUS1_U3_b36_37" : Real;
Fil_BUS1_U12_b38_39 | Real | "Fil_BUS1_U12_b38_39" : Real;
Fil_BUS1_U13_b40_41 | Real | "Fil_BUS1_U13_b40_41" : Real;
Fil_BUS1_U23_b42_43 | Real | "Fil_BUS1_U23_b42_43" : Real;
Fil_BUS1_UAvr_b44_45 | Real | "Fil_BUS1_UAvr_b44_45" : Real;
Fil_BUS2_FR_b46_47 | Real | "Fil_BUS2_FR_b46_47" : Real;
Fil_BUS2_U1_b48_49 | Real | "Fil_BUS2_U1_b48_49" : Real;
Fil_BUS2_U2_b50_51 | Real | "Fil_BUS2_U2_b50_51" : Real;
Fil_BUS2_U3_b52_53 | Real | "Fil_BUS2_U3_b52_53" : Real;
Fil_BUS2_U12_b54_55 | Real | "Fil_BUS2_U12_b54_55" : Real;
Fil_BUS2_U13_b56_57 | Real | "Fil_BUS2_U13_b56_57" : Real;
Fil_BUS2_U23_b58_59 | Real | "Fil_BUS2_U23_b58_59" : Real;
Fil_BUS2_UAvr_b60_61 | Real | "Fil_BUS2_UAvr_b60_61" : Real;
Fil_FDR_I1_b62_63 | Real | "Fil_FDR_I1_b62_63" : Real;
Fil_FDR_I2_b64_65 | Real | "Fil_FDR_I2_b64_65" : Real;
Fil_FDR_I3_b65_67 | Real | "Fil_FDR_I3_b65_67" : Real;
Fil_FDR_IAvr_b68_69 | Real | "Fil_FDR_IAvr_b68_69" : Real;
Fil_FDR_P | Real | "Fil_FDR_P" : Real;
Fil_FDR_Q | Real | "Fil_FDR_Q" : Real;
Fil_FDR_S | Real | "Fil_FDR_S" : Real;
Fil_FDR_PF | Real | "Fil_FDR_PF" : Real;
Fil_FDR_PL1 | Real | "Fil_FDR_PL1" : Real;
Fil_FDR_PL2 | Real | "Fil_FDR_PL2" : Real;
Fil_FDR_PL3 | Real | "Fil_FDR_PL3" : Real;
Fil_FDR_QL1 | Real | "Fil_FDR_QL1" : Real;
Fil_FDR_QL2 | Real | "Fil_FDR_QL2" : Real;
Fil_FDR_QL3 | Real | "Fil_FDR_QL3" : Real;
Fil_FDR_PFL1 | Real | "Fil_FDR_PFL1" : Real;
Fil_FDR_PFL2 | Real | "Fil_FDR_PFL2" : Real;
Fil_FDR_PFL3 | Real | "Fil_FDR_PFL3" : Real;
Fc_FDR_FR_b14_15 | Real | "Fc_FDR_FR_b14_15" : Real;
Fc_FDR_U1_b16_17 | Real | "Fc_FDR_U1_b16_17" : Real;
Fc_FDR_U2_b18_19 | Real | "Fc_FDR_U2_b18_19" : Real;
Fc_FDR_U3_b20_21 | Real | "Fc_FDR_U3_b20_21" : Real;
Fc_FDR_U12_b22_23 | Real | "Fc_FDR_U12_b22_23" : Real;
Fc_FDR_U13_b24_25 | Real | "Fc_FDR_U13_b24_25" : Real;
Fc_FDR_U23_b26_27 | Real | "Fc_FDR_U23_b26_27" : Real;
Fc_FDR_UAvr_b28_29 | Real | "Fc_FDR_UAvr_b28_29" : Real;
Fact_BUS1_FR_b31_32 | Real | "Fact_BUS1_FR_b31_32" : Real;
Fact_BUS1_U1_b32_33 | Real | "Fact_BUS1_U1_b32_33" : Real;
Fact_BUS1_U2_b34_35 | Real | "Fact_BUS1_U2_b34_35" : Real;
Fact_BUS1_U3_b36_37 | Real | "Fact_BUS1_U3_b36_37" : Real;
Fact_BUS1_U12_b38_39 | Real | "Fact_BUS1_U12_b38_39" : Real;
Fact_BUS1_U13_b40_41 | Real | "Fact_BUS1_U13_b40_41" : Real;
Fact_BUS1_U23_b42_43 | Real | "Fact_BUS1_U23_b42_43" : Real;
Fact_BUS1_UAvr_b44_45 | Real | "Fact_BUS1_UAvr_b44_45" : Real;
Fc_BUS2_FR_b46_47 | Real | "Fc_BUS2_FR_b46_47" : Real;
Fc_BUS2_U1_b48_49 | Real | "Fc_BUS2_U1_b48_49" : Real;
Fc_BUS2_U2_b50_51 | Real | "Fc_BUS2_U2_b50_51" : Real;
Fc_BUS2_U3_b52_53 | Real | "Fc_BUS2_U3_b52_53" : Real;
Fc_BUS2_U12_b54_55 | Real | "Fc_BUS2_U12_b54_55" : Real;
Fc_BUS2_U13_b56_57 | Real | "Fc_BUS2_U13_b56_57" : Real;
Fc_BUS2_U23_b58_59 | Real | "Fc_BUS2_U23_b58_59" : Real;
Fc_BUS2_UAvr_b60_61 | Real | "Fc_BUS2_UAvr_b60_61" : Real;
Fc_FDR_I1_b62_63 | Real | "Fc_FDR_I1_b62_63" : Real;
Fc_FDR_I2_b64_65 | Real | "Fc_FDR_I2_b64_65" : Real;
Fc_FDR_I3_b65_67 | Real | "Fc_FDR_I3_b65_67" : Real;
Fc_FDR_IAvr_b68_69 | Real | "Fc_FDR_IAvr_b68_69" : Real;
Fc_FDR_P_b70_71 | Real | "Fc_FDR_P_b70_71" : Real;
Fc_FDR_Q_b72_73 | Real | "Fc_FDR_Q_b72_73" : Real;
Fc_FDR_S_b74_75 | Real | "Fc_FDR_S_b74_75" : Real;
Fc_FDR_PF_b76_77 | Real | "Fc_FDR_PF_b76_77" : Real;
Fc_FDR_PL1_b78_79 | Real | "Fc_FDR_PL1_b78_79" : Real;
Fc_FDR_PL2_b80_81 | Real | "Fc_FDR_PL2_b80_81" : Real;
Fc_FDR_PL3_b82_83 | Real | "Fc_FDR_PL3_b82_83" : Real;
Fc_FDR_QL1_b84_85 | Real | "Fc_FDR_QL1_b84_85" : Real;
Fc_FDR_QL2_b86_87 | Real | "Fc_FDR_QL2_b86_87" : Real;
Fc_FDR_QL3_b88_89 | Real | "Fc_FDR_QL3_b88_89" : Real;
Fc_FDR_PFL1_b90_91 | Real | "Fc_FDR_PFL1_b90_91" : Real;
Fc_FDR_PFL2_b92_93 | Real | "Fc_FDR_PFL2_b92_93" : Real;
Fc_FDR_PFL3_b94_95 | Real | "Fc_FDR_PFL3_b94_95" : Real;
Fc_P_activ_b96_99 | Real | "Fc_P_activ_b96_99" : Real;
Fc_P_obr_b100_103 | Real | "Fc_P_obr_b100_103" : Real;
Fc_P_emk_reakt_b104_107 | Real | "Fc_P_emk_reakt_b104_107" : Real;
Fc_P_ind_reakt_b108_111 | Real | "Fc_P_ind_reakt_b108_111" : Real;
Fc_Io1_b112_113 | Real | "Fc_Io1_b112_113" : Real;
Fc_Uo1_b114_115 | Real | "Fc_Uo1_b114_115" : Real;
Fc_Po1_b116_117 | Real | "Fc_Po1_b116_117" : Real;
Fc_Qo1_b118_119 | Real | "Fc_Qo1_b118_119" : Real;
Fc_Alarm1_b120_121 | Real | "Fc_Alarm1_b120_121" : Real;
Fc_Alarm2_b122_123 | Real | "Fc_Alarm2_b122_123" : Real;
Fc_Alarm3_b124_125 | Real | "Fc_Alarm3_b124_125" : Real;
Fc_Alarm4_b126_127 | Real | "Fc_Alarm4_b126_127" : Real;
Fc_Alarm5_b128_129 | Real | "Fc_Alarm5_b128_129" : Real;
Fc_PM_Gen_number_b130_131 | Real | "Fc_PM_Gen_number_b130_131" : Real;
Fc_PM_BCG_prstatus_b132_133 | Real | "Fc_PM_BCG_prstatus_b132_133" : Real;
Fc_PM_BCG_ownstatus_b134_135 | Real | "Fc_PM_BCG_ownstatus_b134_135" : Real;
Fc_PM_BCG_netstatus_b136_137 | Real | "Fc_PM_BCG_netstatus_b136_137" : Real;
Fc_PM_8_9_b138_139 | Real | "Fc_PM_8_9_b138_139" : Real;
Fc_PM_10_11_b140_141 | Real | "Fc_PM_10_11_b140_141" : Real;
Fc_PM_12_13_b142_143 | Real | "Fc_PM_12_13_b142_143" : Real;
Fc_PM_14_15_b144_145 | Real | "Fc_PM_14_15_b144_145" : Real;
Fc_PM_16_17_b146_147 | Real | "Fc_PM_16_17_b146_147" : Real;
Fc_PM_18_19_b148_149 | Real | "Fc_PM_18_19_b148_149" : Real;
Fc_PM_20_21_b150_151 | Real | "Fc_PM_20_21_b150_151" : Real;
Fc_PM_asym_load_point_b152_153 | Real | "Fc_PM_asym_load_point_b152_153" : Real;
Fc_PM_asym_power_factor_b151_155 | Real | "Fc_PM_asym_power_factor_b151_155" : Real;
Fc_P_kw_b156_157 | Real | "Fc_P_kw_b156_157" : Real;
Fc_P_ps_b158_159 | Real | "Fc_P_ps_b158_159" : Real;
Fc_F_I_amp_b160_161 | Real | "Fc_F_I_amp_b160_161" : Real;
Fc_F_I_ps_b162_163 | Real | "Fc_F_I_ps_b162_163" : Real;
Fc_F_U_b164_165 | Real | "Fc_F_U_b164_165" : Real;
Fc_F_freg_b166_167 | Real | "Fc_F_freg_b166_167" : Real;
Fc_F_cosf_b168_169 | Real | "Fc_F_cosf_b168_169" : Real;
Fc_B1_U_b170_171 | Real | "Fc_B1_U_b170_171" : Real;
Fc_B1_freg1_b172_173 | Real | "Fc_B1_freg1_b172_173" : Real;
Fc_RPM_b174_175 | Real | "Fc_RPM_b174_175" : Real;
Fc_BR1_ON_cycles_b176_177 | Real | "Fc_BR1_ON_cycles_b176_177" : Real;
Fc_BR2_ON_cycles_b178_179 | Real | "Fc_BR2_ON_cycles_b178_179" : Real;
Fc_BR3_ON_cycles_b180_181 | Real | "Fc_BR3_ON_cycles_b180_181" : Real;
Fc_Start_counter_b182_183 | Real | "Fc_Start_counter_b182_183" : Real;
Fc_DP_MD33_R1_b184_185 | Real | "Fc_DP_MD33_R1_b184_185" : Real;
Fc_DP_MD33_R2_b186_187 | Real | "Fc_DP_MD33_R2_b186_187" : Real;
Fc_DP_MD33_R3_b188_189 | Real | "Fc_DP_MD33_R3_b188_189" : Real;
Kf_FDR_FR_b14_15 | Real | "Kf_FDR_FR_b14_15" : Real;
Kf_FDR_U1_b16_17 | Real | "Kf_FDR_U1_b16_17" : Real;
Kf_FDR_U2_b18_19 | Real | "Kf_FDR_U2_b18_19" : Real;
Kf_FDR_U3_b20_21 | Real | "Kf_FDR_U3_b20_21" : Real;
Kf_FDR_U12_b22_23 | Real | "Kf_FDR_U12_b22_23" : Real;
Kf_FDR_U13_b24_25 | Real | "Kf_FDR_U13_b24_25" : Real;
Kf_FDR_U23_b26_27 | Real | "Kf_FDR_U23_b26_27" : Real;
Kf_FDR_UAvr_b28_29 | Real | "Kf_FDR_UAvr_b28_29" : Real;
Kf_BUS1_FR_b31_32 | Real | "Kf_BUS1_FR_b31_32" : Real;
Kf_BUS1_U1_b32_33 | Real | "Kf_BUS1_U1_b32_33" : Real;
Kf_BUS1_U2_b34_35 | Real | "Kf_BUS1_U2_b34_35" : Real;
Kf_BUS1_U3_b36_37 | Real | "Kf_BUS1_U3_b36_37" : Real;
Kf_BUS1_U12_b38_39 | Real | "Kf_BUS1_U12_b38_39" : Real;
Kf_BUS1_U13_b40_41 | Real | "Kf_BUS1_U13_b40_41" : Real;
Kf_BUS1_U23_b42_43 | Real | "Kf_BUS1_U23_b42_43" : Real;
Kf_BUS1_UAvr_b44_45 | Real | "Kf_BUS1_UAvr_b44_45" : Real;
Kf_BUS2_FR_b46_47 | Real | "Kf_BUS2_FR_b46_47" : Real;
Kf_BUS2_U1_b48_49 | Real | "Kf_BUS2_U1_b48_49" : Real;
Kf_BUS2_U2_b50_51 | Real | "Kf_BUS2_U2_b50_51" : Real;
Kf_BUS2_U3_b52_53 | Real | "Kf_BUS2_U3_b52_53" : Real;
Kf_BUS2_U12_b54_55 | Real | "Kf_BUS2_U12_b54_55" : Real;
Kf_BUS2_U13_b56_57 | Real | "Kf_BUS2_U13_b56_57" : Real;
Kf_BUS2_U23_b58_59 | Real | "Kf_BUS2_U23_b58_59" : Real;
Kf_BUS2_UAvr_b60_61 | Real | "Kf_BUS2_UAvr_b60_61" : Real;
Kf_FDR_I1_b62_63 | Real | "Kf_FDR_I1_b62_63" : Real;
Kf_FDR_I2_b64_65 | Real | "Kf_FDR_I2_b64_65" : Real;
Kf_FDR_I3_b65_67 | Real | "Kf_FDR_I3_b65_67" : Real;
Kf_FDR_IAvr_b68_69 | Real | "Kf_FDR_IAvr_b68_69" : Real;
Kf_FDR_P_b70_71 | Real | "Kf_FDR_P_b70_71" : Real;
Kf_FDR_Q_b72_73 | Real | "Kf_FDR_Q_b72_73" : Real;
Kf_FDR_S_b74_75 | Real | "Kf_FDR_S_b74_75" : Real;
Kf_FDR_PF_b76_77 | Real | "Kf_FDR_PF_b76_77" : Real;
Kf_FDR_PL1_b78_79 | Real | "Kf_FDR_PL1_b78_79" : Real;
Kf_FDR_PL2_b80_81 | Real | "Kf_FDR_PL2_b80_81" : Real;
Kf_FDR_PL3_b82_83 | Real | "Kf_FDR_PL3_b82_83" : Real;
Kf_FDR_QL1_b84_85 | Real | "Kf_FDR_QL1_b84_85" : Real;
Kf_FDR_QL2_b86_87 | Real | "Kf_FDR_QL2_b86_87" : Real;
Kf_FDR_QL3_b88_89 | Real | "Kf_FDR_QL3_b88_89" : Real;
Kf_FDR_PFL1_b90_91 | Real | "Kf_FDR_PFL1_b90_91" : Real;
Kf_FDR_PFL2_b92_93 | Real | "Kf_FDR_PFL2_b92_93" : Real;
Kf_FDR_PFL3_b94_95 | Real | "Kf_FDR_PFL3_b94_95" : Real;
Kf_P_activ_b96_99 | Real | "Kf_P_activ_b96_99" : Real;
Kf_P_obr_b100_103 | Real | "Kf_P_obr_b100_103" : Real;
Kf_P_emk_reakt_b104_107 | Real | "Kf_P_emk_reakt_b104_107" : Real;
Kf_P_ind_reakt_b108_111 | Real | "Kf_P_ind_reakt_b108_111" : Real;
Kf_Io1_b112_113 | Real | "Kf_Io1_b112_113" : Real;
Kf_Uo1_b114_115 | Real | "Kf_Uo1_b114_115" : Real;
Kf_Po1_b116_117 | Real | "Kf_Po1_b116_117" : Real;
Kf_Qo1_b118_119 | Real | "Kf_Qo1_b118_119" : Real;
Kf_Alarm1_b120_121 | Real | "Kf_Alarm1_b120_121" : Real;
Kf_Alarm2_b122_123 | Real | "Kf_Alarm2_b122_123" : Real;
Kf_Alarm3_b124_125 | Real | "Kf_Alarm3_b124_125" : Real;
Kf_Alarm4_b126_127 | Real | "Kf_Alarm4_b126_127" : Real;
Kf_Alarm5_b128_129 | Real | "Kf_Alarm5_b128_129" : Real;
Kf_PM_Gen_number_b130_131 | Real | "Kf_PM_Gen_number_b130_131" : Real;
Kf_PM_BCG_prstatus_b132_133 | Real | "Kf_PM_BCG_prstatus_b132_133" : Real;
Kf_PM_BCG_ownstatus_b134_135 | Real | "Kf_PM_BCG_ownstatus_b134_135" : Real;
Kf_PM_BCG_netstatus_b136_137 | Real | "Kf_PM_BCG_netstatus_b136_137" : Real;
Kf_PM_8_9_b138_139 | Real | "Kf_PM_8_9_b138_139" : Real;
Kf_PM_10_11_b140_141 | Real | "Kf_PM_10_11_b140_141" : Real;
Kf_PM_12_13_b142_143 | Real | "Kf_PM_12_13_b142_143" : Real;
Kf_PM_14_15_b144_145 | Real | "Kf_PM_14_15_b144_145" : Real;
Kf_PM_16_17_b146_147 | Real | "Kf_PM_16_17_b146_147" : Real;
Kf_PM_18_19_b148_149 | Real | "Kf_PM_18_19_b148_149" : Real;
Kf_PM_20_21_b150_151 | Real | "Kf_PM_20_21_b150_151" : Real;
Kf_PM_asym_load_point_b152_153 | Real | "Kf_PM_asym_load_point_b152_153" : Real;
Kf_PM_asym_power_factor_b151_155 | Real | "Kf_PM_asym_power_factor_b151_155" : Real;
Kf_P_kw_b156_157 | Real | "Kf_P_kw_b156_157" : Real;
Kf_P_ps_b158_159 | Real | "Kf_P_ps_b158_159" : Real;
Kf_F_I_amp_b160_161 | Real | "Kf_F_I_amp_b160_161" : Real;
Kf_F_I_ps_b162_163 | Real | "Kf_F_I_ps_b162_163" : Real;
Kf_F_U_b164_165 | Real | "Kf_F_U_b164_165" : Real;
Kf_F_freg_b166_167 | Real | "Kf_F_freg_b166_167" : Real;
Kf_F_cosf_b168_169 | Real | "Kf_F_cosf_b168_169" : Real;
Kf_B1_U_b170_171 | Real | "Kf_B1_U_b170_171" : Real;
Kf_B1_freg1_b172_173 | Real | "Kf_B1_freg1_b172_173" : Real;
Kf_RPM_b174_175 | Real | "Kf_RPM_b174_175" : Real;
Kf_BR1_ON_cycles_b176_177 | Real | "Kf_BR1_ON_cycles_b176_177" : Real;
Kf_BR2_ON_cycles_b178_179 | Real | "Kf_BR2_ON_cycles_b178_179" : Real;
Kf_BR3_ON_cycles_b180_181 | Real | "Kf_BR3_ON_cycles_b180_181" : Real;
Kf_Start_counter_b182_183 | Real | "Kf_Start_counter_b182_183" : Real;
Kf_DP_MD33_R1_b184_185 | Real | "Kf_DP_MD33_R1_b184_185" : Real;
Kf_DP_MD33_R2_b186_187 | Real | "Kf_DP_MD33_R2_b186_187" : Real;
Kf_DP_MD33_R3_b188_189 | Real | "Kf_DP_MD33_R3_b188_189" : Real;

## Для UDT Libr
Name | Comunication drive | HMI DataType | Length | Start value | offset | bit offset
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_350(1) | SIMATIC S7 300/400 | Bool | 1 |  | 0 | 0 | 0 | 10 | 0 | 100
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_351(1) | SIMATIC S7 300/400 | Bool | 1 |  | 0 | 1 | 0 | 10 | 0 | 100
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_352(1) | SIMATIC S7 300/400 | Bool | 1 |  | 0 | 2 | 0 | 10 | 0 | 100
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_353(1) | SIMATIC S7 300/400 | Bool | 1 |  | 0 | 3 | 0 | 10 | 0 | 100
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_354(1) | SIMATIC S7 300/400 | Bool | 1 |  | 0 | 4 | 0 | 10 | 0 | 100
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_355(1) | SIMATIC S7 300/400 | Bool | 1 |  | 0 | 5 | 0 | 10 | 0 | 100
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_356(1) | SIMATIC S7 300/401 | Bool | 1 |  | 0 | 6 | 0 | 10 | 0 | 100
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_357(1) | SIMATIC S7 300/402 | Bool | 1 |  | 0 | 7 | 0 | 10 | 0 | 100
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_358(1) | SIMATIC S7 300/403 | Bool | 1 |  | 1 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_359(1) | SIMATIC S7 300/404 | Bool | 1 |  | 1 | 1
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_360(1) | SIMATIC S7 300/405 | Bool | 1 |  | 1 | 2
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_361(1) | SIMATIC S7 300/406 | Bool | 1 |  | 1 | 3
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_362(1) | SIMATIC S7 300/407 | Bool | 1 |  | 1 | 4
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_363(1) | SIMATIC S7 300/408 | Bool | 1 |  | 1 | 5
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_364(1) | SIMATIC S7 300/409 | Bool | 1 |  | 1 | 6
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_365(1) | SIMATIC S7 300/410 | Bool | 1 |  | 1 | 7
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_Change_work(1) | SIMATIC S7 300/411 | Bool | 1 |  | 2 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_Res(1) | SIMATIC S7 300/412 | Bool | 1 |  | 2 | 1
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_Set_time(1) | SIMATIC S7 300/413 | Bool | 1 |  | 2 | 2
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_Cb3(1) | SIMATIC S7 300/414 | Bool | 1 |  | 2 | 3
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_Cb4(1) | SIMATIC S7 300/415 | Bool | 1 |  | 2 | 4
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_Cb5(1) | SIMATIC S7 300/416 | Bool | 1 |  | 2 | 5
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_Cb6(1) | SIMATIC S7 300/417 | Bool | 1 |  | 2 | 6
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_Cb7(1) | SIMATIC S7 300/418 | Bool | 1 |  | 2 | 7
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_local(1) | SIMATIC S7 300/419 | Bool | 1 |  | 3 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_remote(1) | SIMATIC S7 300/420 | Bool | 1 |  | 3 | 1
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_SCADA(1) | SIMATIC S7 300/421 | Bool | 1 |  | 3 | 2
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_test_local(1) | SIMATIC S7 300/422 | Bool | 1 |  | 3 | 3
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_test_remote(1) | SIMATIC S7 300/423 | Bool | 1 |  | 3 | 4
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_NM5(1) | SIMATIC S7 300/424 | Bool | 1 |  | 3 | 5
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_NM6(1) | SIMATIC S7 300/425 | Bool | 1 |  | 3 | 6
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Control_Byte_b2_3_NM7(1) | SIMATIC S7 300/426 | Bool | 1 |  | 3 | 7
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Time_set_b4_11_month(1) | SIMATIC S7 300/427 | USInt | 1 |  | 4 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Time_set_b4_11_year(1) | SIMATIC S7 300/428 | USInt | 1 |  | 5 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Time_set_b4_11_hour(1) | SIMATIC S7 300/429 | USInt | 1 |  | 6 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Time_set_b4_11_day(1) | SIMATIC S7 300/430 | USInt | 1 |  | 7 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Time_set_b4_11_second(1) | SIMATIC S7 300/431 | USInt | 1 |  | 8 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Time_set_b4_11_minute(1) | SIMATIC S7 300/432 | USInt | 1 |  | 9 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Time_set_b4_11_millisecondhigh_Byte(1) | SIMATIC S7 300/433 | USInt | 1 |  | 10 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_1_b0_11_Time_set_b4_11_millisecondlow_Byte(1) | SIMATIC S7 300/434 | USInt | 1 |  | 11 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_30_b12_15_instr_No_1_b5(1) | SIMATIC S7 300/435 | USInt | 1 |  | 12 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_30_b12_15_instr_No_2_b6(1) | SIMATIC S7 300/436 | USInt | 1 |  | 13 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_30_b12_15_Data_val_1_b7(1) | SIMATIC S7 300/437 | USInt | 1 |  | 14 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Out_module_30_b12_15_Data_val_2_b8(1) | SIMATIC S7 300/438 | USInt | 1 |  | 15 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_FR_b14_15(1) | SIMATIC S7 300/439 | Real | 1 |  | 16 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_U1_b16_17(1) | SIMATIC S7 300/440 | Real | 1 |  | 20 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_U2_b18_19(1) | SIMATIC S7 300/441 | Real | 1 |  | 24 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_U3_b20_21(1) | SIMATIC S7 300/442 | Real | 1 |  | 28 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_U12_b22_23(1) | SIMATIC S7 300/443 | Real | 1 |  | 32 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_U13_b24_25(1) | SIMATIC S7 300/444 | Real | 1 |  | 36 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_U23_b26_27(1) | SIMATIC S7 300/445 | Real | 1 |  | 40 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_UAvr_b28_29(1) | SIMATIC S7 300/446 | Real | 1 |  | 44 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS1_FR_b31_32(1) | SIMATIC S7 300/447 | Real | 1 |  | 48 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS1_U1_b32_33(1) | SIMATIC S7 300/448 | Real | 1 |  | 52 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS1_U2_b34_35(1) | SIMATIC S7 300/449 | Real | 1 |  | 56 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS1_U3_b36_37(1) | SIMATIC S7 300/450 | Real | 1 |  | 60 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS1_U12_b38_39(1) | SIMATIC S7 300/451 | Real | 1 |  | 64 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS1_U13_b40_41(1) | SIMATIC S7 300/452 | Real | 1 |  | 68 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS1_U23_b42_43(1) | SIMATIC S7 300/453 | Real | 1 |  | 72 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS1_UAvr_b44_45(1) | SIMATIC S7 300/454 | Real | 1 |  | 76 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS2_FR_b46_47(1) | SIMATIC S7 300/455 | Real | 1 |  | 80 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS2_U1_b48_49(1) | SIMATIC S7 300/456 | Real | 1 |  | 84 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS2_U2_b50_51(1) | SIMATIC S7 300/457 | Real | 1 |  | 88 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS2_U3_b52_53(1) | SIMATIC S7 300/458 | Real | 1 |  | 92 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS2_U12_b54_55(1) | SIMATIC S7 300/459 | Real | 1 |  | 96 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS2_U13_b56_57(1) | SIMATIC S7 300/460 | Real | 1 |  | 100 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS2_U23_b58_59(1) | SIMATIC S7 300/461 | Real | 1 |  | 104 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_BUS2_UAvr_b60_61(1) | SIMATIC S7 300/462 | Real | 1 |  | 108 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_I1_b62_63(1) | SIMATIC S7 300/463 | Real | 1 |  | 112 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_I2_b64_65(1) | SIMATIC S7 300/464 | Real | 1 |  | 116 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_I3_b65_67(1) | SIMATIC S7 300/465 | Real | 1 |  | 120 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_IAvr_b68_69(1) | SIMATIC S7 300/466 | Real | 1 |  | 124 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_P(1) | SIMATIC S7 300/467 | Real | 1 |  | 128 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_Q(1) | SIMATIC S7 300/468 | Real | 1 |  | 132 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_S(1) | SIMATIC S7 300/469 | Real | 1 |  | 136 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_PF(1) | SIMATIC S7 300/470 | Real | 1 |  | 140 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_PL1(1) | SIMATIC S7 300/471 | Real | 1 |  | 144 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_PL2(1) | SIMATIC S7 300/472 | Real | 1 |  | 148 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_PL3(1) | SIMATIC S7 300/473 | Real | 1 |  | 152 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_QL1(1) | SIMATIC S7 300/474 | Real | 1 |  | 156 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_QL2(1) | SIMATIC S7 300/475 | Real | 1 |  | 160 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_QL3(1) | SIMATIC S7 300/476 | Real | 1 |  | 164 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_PFL1(1) | SIMATIC S7 300/477 | Real | 1 |  | 168 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_PFL2(1) | SIMATIC S7 300/478 | Real | 1 |  | 172 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Filtered_FDR_PFL3(1) | SIMATIC S7 300/479 | Real | 1 |  | 176 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_7_b14_29_Fc_FDR_FR_b14_15(1) | SIMATIC S7 300/480 | Real | 1 |  | 180 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_7_b14_29_Fc_FDR_U1_b16_17(1) | SIMATIC S7 300/481 | Real | 1 |  | 184 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_7_b14_29_Fc_FDR_U2_b18_19(1) | SIMATIC S7 300/482 | Real | 1 |  | 188 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_7_b14_29_Fc_FDR_U3_b20_21(1) | SIMATIC S7 300/483 | Real | 1 |  | 192 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_7_b14_29_Fc_FDR_U12_b22_23(1) | SIMATIC S7 300/484 | Real | 1 |  | 196 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_7_b14_29_Fc_FDR_U13_b24_25(1) | SIMATIC S7 300/485 | Real | 1 |  | 200 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_7_b14_29_Fc_FDR_U23_b26_27(1) | SIMATIC S7 300/486 | Real | 1 |  | 204 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_7_b14_29_Fc_FDR_UAvr_b28_29(1) | SIMATIC S7 300/487 | Real | 1 |  | 208 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_830_45_Fc_BUS1_FR_b31_32(1) | SIMATIC S7 300/488 | Real | 1 |  | 212 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_830_45_Fc_BUS1_U1_b32_33(1) | SIMATIC S7 300/489 | Real | 1 |  | 216 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_830_45_Fc_BUS1_U2_b34_35(1) | SIMATIC S7 300/490 | Real | 1 |  | 220 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_830_45_Fc_BUS1_U3_b36_37(1) | SIMATIC S7 300/491 | Real | 1 |  | 224 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_830_45_Fc_BUS1_U12_b38_39(1) | SIMATIC S7 300/492 | Real | 1 |  | 228 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_830_45_Fc_BUS1_U13_b40_41(1) | SIMATIC S7 300/493 | Real | 1 |  | 232 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_830_45_Fc_BUS1_U23_b42_43(1) | SIMATIC S7 300/494 | Real | 1 |  | 236 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_830_45_Fc_BUS1_UAvr_b44_45(1) | SIMATIC S7 300/495 | Real | 1 |  | 240 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_9_b46_61_Fc_BUS2_FR_b46_47(1) | SIMATIC S7 300/496 | Real | 1 |  | 244 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_9_b46_61_Fc_BUS2_U1_b48_49(1) | SIMATIC S7 300/497 | Real | 1 |  | 248 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_9_b46_61_Fc_BUS2_U2_b50_51(1) | SIMATIC S7 300/498 | Real | 1 |  | 252 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_9_b46_61_Fc_BUS2_U3_b52_53(1) | SIMATIC S7 300/499 | Real | 1 |  | 256 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_9_b46_61_Fc_BUS2_U12_b54_55(1) | SIMATIC S7 300/500 | Real | 1 |  | 260 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_9_b46_61_Fc_BUS2_U13_b56_57(1) | SIMATIC S7 300/501 | Real | 1 |  | 264 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_9_b46_61_Fc_BUS2_U23_b58_59(1) | SIMATIC S7 300/502 | Real | 1 |  | 268 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_9_b46_61_Fc_BUS2_UAvr_b60_61(1) | SIMATIC S7 300/503 | Real | 1 |  | 272 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_10_b62_69_Fc_FDR_I1_b62_63(1) | SIMATIC S7 300/504 | Real | 1 |  | 276 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_10_b62_69_Fc_FDR_I2_b64_65(1) | SIMATIC S7 300/505 | Real | 1 |  | 280 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_10_b62_69_Fc_FDR_I3_b65_67(1) | SIMATIC S7 300/506 | Real | 1 |  | 284 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_10_b62_69_Fc_FDR_IAvr_b68_69(1) | SIMATIC S7 300/507 | Real | 1 |  | 288 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_12_b70_77_Fc_FDR_P_b70_71(1) | SIMATIC S7 300/508 | Real | 1 |  | 292 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_12_b70_77_Fc_FDR_Q_b72_73(1) | SIMATIC S7 300/509 | Real | 1 |  | 296 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_12_b70_77_Fc_FDR_S_b74_75(1) | SIMATIC S7 300/510 | Real | 1 |  | 300 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_12_b70_77_Fc_FDR_PF_b76_77(1) | SIMATIC S7 300/511 | Real | 1 |  | 304 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_13_b78_83_Fc_FDR_PL1_b78_79(1) | SIMATIC S7 300/512 | Real | 1 |  | 308 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_13_b78_83_Fc_FDR_PL2_b80_81(1) | SIMATIC S7 300/513 | Real | 1 |  | 312 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_13_b78_83_Fc_FDR_PL3_b82_83(1) | SIMATIC S7 300/514 | Real | 1 |  | 316 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_14_b84_89_Fc_FDR_QL1_b84_85(1) | SIMATIC S7 300/515 | Real | 1 |  | 320 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_14_b84_89_Fc_FDR_QL2_b86_87(1) | SIMATIC S7 300/516 | Real | 1 |  | 324 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_14_b84_89_Fc_FDR_QL3_b88_89(1) | SIMATIC S7 300/517 | Real | 1 |  | 328 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_15_b90_95_Fc_FDR_PFL1_b90_91(1) | SIMATIC S7 300/518 | Real | 1 |  | 332 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_15_b90_95_Fc_FDR_PFL2_b92_93(1) | SIMATIC S7 300/519 | Real | 1 |  | 336 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_15_b90_95_Fc_FDR_PFL3_b94_95(1) | SIMATIC S7 300/520 | Real | 1 |  | 340 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_18_b96_111_Fc_P_activ_b96_99(1) | SIMATIC S7 300/521 | Real | 1 |  | 344 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_18_b96_111_Fc_P_obr_b100_103(1) | SIMATIC S7 300/522 | Real | 1 |  | 348 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_18_b96_111_Fc_P_emk_reakt_b104_107(1) | SIMATIC S7 300/523 | Real | 1 |  | 352 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_18_b96_111_Fc_P_ind_reakt_b108_111(1) | SIMATIC S7 300/524 | Real | 1 |  | 356 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_16_b112_119_Fc_Io1_b112_113(1) | SIMATIC S7 300/525 | Real | 1 |  | 360 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_16_b112_119_Fc_Uo1_b114_115(1) | SIMATIC S7 300/526 | Real | 1 |  | 364 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_16_b112_119_Fc_Po1_b116_117(1) | SIMATIC S7 300/527 | Real | 1 |  | 368 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_16_b112_119_Fc_Qo1_b118_119(1) | SIMATIC S7 300/528 | Real | 1 |  | 372 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_25_b120_129_Fc_Alarm1_b120_121(1) | SIMATIC S7 300/529 | Real | 1 |  | 376 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_25_b120_129_Fc_Alarm2_b122_123(1) | SIMATIC S7 300/530 | Real | 1 |  | 380 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_25_b120_129_Fc_Alarm3_b124_125(1) | SIMATIC S7 300/531 | Real | 1 |  | 384 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_25_b120_129_Fc_Alarm4_b126_127(1) | SIMATIC S7 300/532 | Real | 1 |  | 388 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_25_b120_129_Fc_Alarm5_b128_129(1) | SIMATIC S7 300/533 | Real | 1 |  | 392 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_Gen_number_b130_131(1) | SIMATIC S7 300/534 | Real | 1 |  | 396 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_BCG_prstatus_b132_133(1) | SIMATIC S7 300/535 | Real | 1 |  | 400 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_BCG_ownstatus_b134_135(1) | SIMATIC S7 300/536 | Real | 1 |  | 404 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_BCG_netstatus_b136_137(1) | SIMATIC S7 300/537 | Real | 1 |  | 408 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_8_9_b138_139(1) | SIMATIC S7 300/538 | Real | 1 |  | 412 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_10_11_b140_141(1) | SIMATIC S7 300/539 | Real | 1 |  | 416 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_12_13_b142_143(1) | SIMATIC S7 300/540 | Real | 1 |  | 420 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_14_15_b144_145(1) | SIMATIC S7 300/541 | Real | 1 |  | 424 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_16_17_b146_147(1) | SIMATIC S7 300/542 | Real | 1 |  | 428 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_18_19_b148_149(1) | SIMATIC S7 300/543 | Real | 1 |  | 432 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_20_21_b150_151(1) | SIMATIC S7 300/544 | Real | 1 |  | 436 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_asym_load_point_b152_153(1) | SIMATIC S7 300/545 | Real | 1 |  | 440 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_31_b130_155_Fc_PM_asym_power_factor_b151_155(1) | SIMATIC S7 300/546 | Real | 1 |  | 444 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_32_b156_173_Fc_P_kw_b156_157(1) | SIMATIC S7 300/547 | Real | 1 |  | 448 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_32_b156_173_Fc_P_ps_b158_159(1) | SIMATIC S7 300/548 | Real | 1 |  | 452 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_32_b156_173_Fc_F_I_amp_b160_161(1) | SIMATIC S7 300/549 | Real | 1 |  | 456 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_32_b156_173_Fc_F_I_ps_b162_163(1) | SIMATIC S7 300/550 | Real | 1 |  | 460 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_32_b156_173_Fc_F_U_b164_165(1) | SIMATIC S7 300/551 | Real | 1 |  | 464 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_32_b156_173_Fc_F_freg_b166_167(1) | SIMATIC S7 300/552 | Real | 1 |  | 468 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_32_b156_173_Fc_F_cosf_b168_169(1) | SIMATIC S7 300/553 | Real | 1 |  | 472 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_32_b156_173_Fc_B1_U_b170_171(1) | SIMATIC S7 300/554 | Real | 1 |  | 476 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_32_b156_173_Fc_B1_freg1_b172_173(1) | SIMATIC S7 300/555 | Real | 1 |  | 480 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_33_b174_189_Fc_RPM_b174_175(1) | SIMATIC S7 300/556 | Real | 1 |  | 484 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_33_b174_189_Fc_BR1_ON_cycles_b176_177(1) | SIMATIC S7 300/557 | Real | 1 |  | 488 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_33_b174_189_Fc_BR2_ON_cycles_b178_179(1) | SIMATIC S7 300/558 | Real | 1 |  | 492 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_33_b174_189_Fc_BR3_ON_cycles_b180_181(1) | SIMATIC S7 300/559 | Real | 1 |  | 496 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_33_b174_189_Fc_Start_counter_b182_183(1) | SIMATIC S7 300/560 | Real | 1 |  | 500 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_33_b174_189_Fc_DP_MD33_R1_b184_185(1) | SIMATIC S7 300/561 | Real | 1 |  | 504 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_33_b174_189_Fc_DP_MD33_R2_b186_187(1) | SIMATIC S7 300/562 | Real | 1 |  | 508 | 0
Read_write_Symap_Db_Devices{2}_Wincc_Factor_modul_33_b174_189_Fc_DP_MD33_R3_b188_189(1) | SIMATIC S7 300/563 | Real | 1 |  | 512 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_7_b14_29_Fc_FDR_FR_b14_15(1) | SIMATIC S7 300/564 | Real | 1 |  | 516 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_7_b14_29_Fc_FDR_U1_b16_17(1) | SIMATIC S7 300/565 | Real | 1 |  | 520 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_7_b14_29_Fc_FDR_U2_b18_19(1) | SIMATIC S7 300/566 | Real | 1 |  | 524 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_7_b14_29_Fc_FDR_U3_b20_21(1) | SIMATIC S7 300/567 | Real | 1 |  | 528 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_7_b14_29_Fc_FDR_U12_b22_23(1) | SIMATIC S7 300/568 | Real | 1 |  | 532 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_7_b14_29_Fc_FDR_U13_b24_25(1) | SIMATIC S7 300/569 | Real | 1 |  | 536 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_7_b14_29_Fc_FDR_U23_b26_27(1) | SIMATIC S7 300/570 | Real | 1 |  | 540 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_7_b14_29_Fc_FDR_UAvr_b28_29(1) | SIMATIC S7 300/571 | Real | 1 |  | 544 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_830_45_Fc_BUS1_FR_b31_32(1) | SIMATIC S7 300/572 | Real | 1 |  | 548 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_830_45_Fc_BUS1_U1_b32_33(1) | SIMATIC S7 300/573 | Real | 1 |  | 552 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_830_45_Fc_BUS1_U2_b34_35(1) | SIMATIC S7 300/574 | Real | 1 |  | 556 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_830_45_Fc_BUS1_U3_b36_37(1) | SIMATIC S7 300/575 | Real | 1 |  | 560 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_830_45_Fc_BUS1_U12_b38_39(1) | SIMATIC S7 300/576 | Real | 1 |  | 564 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_830_45_Fc_BUS1_U13_b40_41(1) | SIMATIC S7 300/577 | Real | 1 |  | 568 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_830_45_Fc_BUS1_U23_b42_43(1) | SIMATIC S7 300/578 | Real | 1 |  | 572 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_830_45_Fc_BUS1_UAvr_b44_45(1) | SIMATIC S7 300/579 | Real | 1 |  | 576 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_9_b46_61_Fc_BUS2_FR_b46_47(1) | SIMATIC S7 300/580 | Real | 1 |  | 580 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_9_b46_61_Fc_BUS2_U1_b48_49(1) | SIMATIC S7 300/581 | Real | 1 |  | 584 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_9_b46_61_Fc_BUS2_U2_b50_51(1) | SIMATIC S7 300/582 | Real | 1 |  | 588 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_9_b46_61_Fc_BUS2_U3_b52_53(1) | SIMATIC S7 300/583 | Real | 1 |  | 592 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_9_b46_61_Fc_BUS2_U12_b54_55(1) | SIMATIC S7 300/584 | Real | 1 |  | 596 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_9_b46_61_Fc_BUS2_U13_b56_57(1) | SIMATIC S7 300/585 | Real | 1 |  | 600 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_9_b46_61_Fc_BUS2_U23_b58_59(1) | SIMATIC S7 300/586 | Real | 1 |  | 604 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_9_b46_61_Fc_BUS2_UAvr_b60_61(1) | SIMATIC S7 300/587 | Real | 1 |  | 608 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_10_b62_69_Fc_FDR_I1_b62_63(1) | SIMATIC S7 300/588 | Real | 1 |  | 612 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_10_b62_69_Fc_FDR_I2_b64_65(1) | SIMATIC S7 300/589 | Real | 1 |  | 616 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_10_b62_69_Fc_FDR_I3_b65_67(1) | SIMATIC S7 300/590 | Real | 1 |  | 620 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_10_b62_69_Fc_FDR_IAvr_b68_69(1) | SIMATIC S7 300/591 | Real | 1 |  | 624 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_12_b70_77_Fc_FDR_P_b70_71(1) | SIMATIC S7 300/592 | Real | 1 |  | 628 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_12_b70_77_Fc_FDR_Q_b72_73(1) | SIMATIC S7 300/593 | Real | 1 |  | 632 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_12_b70_77_Fc_FDR_S_b74_75(1) | SIMATIC S7 300/594 | Real | 1 |  | 636 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_12_b70_77_Fc_FDR_PF_b76_77(1) | SIMATIC S7 300/595 | Real | 1 |  | 640 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_13_b78_83_Fc_FDR_PL1_b78_79(1) | SIMATIC S7 300/596 | Real | 1 |  | 644 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_13_b78_83_Fc_FDR_PL2_b80_81(1) | SIMATIC S7 300/597 | Real | 1 |  | 648 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_13_b78_83_Fc_FDR_PL3_b82_83(1) | SIMATIC S7 300/598 | Real | 1 |  | 652 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_14_b84_89_Fc_FDR_QL1_b84_85(1) | SIMATIC S7 300/599 | Real | 1 |  | 656 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_14_b84_89_Fc_FDR_QL2_b86_87(1) | SIMATIC S7 300/600 | Real | 1 |  | 660 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_14_b84_89_Fc_FDR_QL3_b88_89(1) | SIMATIC S7 300/601 | Real | 1 |  | 664 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_15_b90_95_Fc_FDR_PFL1_b90_91(1) | SIMATIC S7 300/602 | Real | 1 |  | 668 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_15_b90_95_Fc_FDR_PFL2_b92_93(1) | SIMATIC S7 300/603 | Real | 1 |  | 672 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_15_b90_95_Fc_FDR_PFL3_b94_95(1) | SIMATIC S7 300/604 | Real | 1 |  | 676 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_18_b96_111_Fc_P_activ_b96_99(1) | SIMATIC S7 300/605 | Real | 1 |  | 680 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_18_b96_111_Fc_P_obr_b100_103(1) | SIMATIC S7 300/606 | Real | 1 |  | 684 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_18_b96_111_Fc_P_emk_reakt_b104_107(1) | SIMATIC S7 300/607 | Real | 1 |  | 688 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_18_b96_111_Fc_P_ind_reakt_b108_111(1) | SIMATIC S7 300/608 | Real | 1 |  | 692 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_16_b112_119_Fc_Io1_b112_113(1) | SIMATIC S7 300/609 | Real | 1 |  | 696 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_16_b112_119_Fc_Uo1_b114_115(1) | SIMATIC S7 300/610 | Real | 1 |  | 700 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_16_b112_119_Fc_Po1_b116_117(1) | SIMATIC S7 300/611 | Real | 1 |  | 704 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_16_b112_119_Fc_Qo1_b118_119(1) | SIMATIC S7 300/612 | Real | 1 |  | 708 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_25_b120_129_Fc_Alarm1_b120_121(1) | SIMATIC S7 300/613 | Real | 1 |  | 712 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_25_b120_129_Fc_Alarm2_b122_123(1) | SIMATIC S7 300/614 | Real | 1 |  | 716 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_25_b120_129_Fc_Alarm3_b124_125(1) | SIMATIC S7 300/615 | Real | 1 |  | 720 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_25_b120_129_Fc_Alarm4_b126_127(1) | SIMATIC S7 300/616 | Real | 1 |  | 724 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_25_b120_129_Fc_Alarm5_b128_129(1) | SIMATIC S7 300/617 | Real | 1 |  | 728 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_Gen_number_b130_131(1) | SIMATIC S7 300/618 | Real | 1 |  | 732 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_BCG_prstatus_b132_133(1) | SIMATIC S7 300/619 | Real | 1 |  | 736 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_BCG_ownstatus_b134_135(1) | SIMATIC S7 300/620 | Real | 1 |  | 740 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_BCG_netstatus_b136_137(1) | SIMATIC S7 300/621 | Real | 1 |  | 744 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_8_9_b138_139(1) | SIMATIC S7 300/622 | Real | 1 |  | 748 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_10_11_b140_141(1) | SIMATIC S7 300/623 | Real | 1 |  | 752 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_12_13_b142_143(1) | SIMATIC S7 300/624 | Real | 1 |  | 756 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_14_15_b144_145(1) | SIMATIC S7 300/625 | Real | 1 |  | 760 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_16_17_b146_147(1) | SIMATIC S7 300/626 | Real | 1 |  | 764 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_18_19_b148_149(1) | SIMATIC S7 300/627 | Real | 1 |  | 768 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_20_21_b150_151(1) | SIMATIC S7 300/628 | Real | 1 |  | 772 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_asym_load_point_b152_153(1) | SIMATIC S7 300/629 | Real | 1 |  | 776 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_31_b130_155_Fc_PM_asym_power_factor_b151_155(1) | SIMATIC S7 300/630 | Real | 1 |  | 780 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_32_b156_173_Fc_P_kw_b156_157(1) | SIMATIC S7 300/631 | Real | 1 |  | 784 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_32_b156_173_Fc_P_ps_b158_159(1) | SIMATIC S7 300/632 | Real | 1 |  | 788 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_32_b156_173_Fc_F_I_amp_b160_161(1) | SIMATIC S7 300/633 | Real | 1 |  | 792 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_32_b156_173_Fc_F_I_ps_b162_163(1) | SIMATIC S7 300/634 | Real | 1 |  | 796 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_32_b156_173_Fc_F_U_b164_165(1) | SIMATIC S7 300/635 | Real | 1 |  | 800 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_32_b156_173_Fc_F_freg_b166_167(1) | SIMATIC S7 300/636 | Real | 1 |  | 804 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_32_b156_173_Fc_F_cosf_b168_169(1) | SIMATIC S7 300/637 | Real | 1 |  | 808 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_32_b156_173_Fc_B1_U_b170_171(1) | SIMATIC S7 300/638 | Real | 1 |  | 812 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_32_b156_173_Fc_B1_freg1_b172_173(1) | SIMATIC S7 300/639 | Real | 1 |  | 816 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_33_b174_189_Fc_RPM_b174_175(1) | SIMATIC S7 300/640 | Real | 1 |  | 820 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_33_b174_189_Fc_BR1_ON_cycles_b176_177(1) | SIMATIC S7 300/641 | Real | 1 |  | 824 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_33_b174_189_Fc_BR2_ON_cycles_b178_179(1) | SIMATIC S7 300/642 | Real | 1 |  | 828 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_33_b174_189_Fc_BR3_ON_cycles_b180_181(1) | SIMATIC S7 300/643 | Real | 1 |  | 832 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_33_b174_189_Fc_Start_counter_b182_183(1) | SIMATIC S7 300/644 | Real | 1 |  | 836 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_33_b174_189_Fc_DP_MD33_R1_b184_185(1) | SIMATIC S7 300/645 | Real | 1 |  | 840 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_33_b174_189_Fc_DP_MD33_R2_b186_187(1) | SIMATIC S7 300/646 | Real | 1 |  | 844 | 0
Read_write_Symap_Db_Devices{2}_Wincc_K_Filter_modul_33_b174_189_Fc_DP_MD33_R3_b188_189(1) | SIMATIC S7 300/647 | Real | 1 |  | 848 | 0

## Для UDT Libr (2)
Name | Comunication drive | HMI DataType | Length | Start value | offset | bit offset
b0_1_event_350 | SIMATIC S7 300/400 | Bool | 1 |  | 0 | 0 | 0 | 10 | 0 | 100
b0_1_event_351 | SIMATIC S7 300/400 | Bool | 1 |  | 0 | 1 | 0 | 10 | 0 | 100
b0_1_event_352 | SIMATIC S7 300/400 | Bool | 1 |  | 0 | 2 | 0 | 10 | 0 | 100
b0_1_event_353 | SIMATIC S7 300/400 | Bool | 1 |  | 0 | 3 | 0 | 10 | 0 | 100
b0_1_event_354 | SIMATIC S7 300/400 | Bool | 1 |  | 0 | 4 | 0 | 10 | 0 | 100
b0_1_event_355 | SIMATIC S7 300/400 | Bool | 1 |  | 0 | 5 | 0 | 10 | 0 | 100
b0_1_event_356 | SIMATIC S7 300/401 | Bool | 1 |  | 0 | 6 | 0 | 10 | 0 | 100
b0_1_event_357 | SIMATIC S7 300/402 | Bool | 1 |  | 0 | 7 | 0 | 10 | 0 | 100
b0_1_event_358 | SIMATIC S7 300/403 | Bool | 1 |  | 1 | 0
b0_1_event_359 | SIMATIC S7 300/404 | Bool | 1 |  | 1 | 1
b0_1_event_360 | SIMATIC S7 300/405 | Bool | 1 |  | 1 | 2
b0_1_event_361 | SIMATIC S7 300/406 | Bool | 1 |  | 1 | 3
b0_1_event_362 | SIMATIC S7 300/407 | Bool | 1 |  | 1 | 4
b0_1_event_363 | SIMATIC S7 300/408 | Bool | 1 |  | 1 | 5
b0_1_event_364 | SIMATIC S7 300/409 | Bool | 1 |  | 1 | 6
b0_1_event_365 | SIMATIC S7 300/410 | Bool | 1 |  | 1 | 7
Change_work | SIMATIC S7 300/411 | Bool | 1 |  | 2 | 0
Res | SIMATIC S7 300/412 | Bool | 1 |  | 2 | 1
Set_time | SIMATIC S7 300/413 | Bool | 1 |  | 2 | 2
Cb3 | SIMATIC S7 300/414 | Bool | 1 |  | 2 | 3
Cb4 | SIMATIC S7 300/415 | Bool | 1 |  | 2 | 4
Cb5 | SIMATIC S7 300/416 | Bool | 1 |  | 2 | 5
Cb6 | SIMATIC S7 300/417 | Bool | 1 |  | 2 | 6
Cb7 | SIMATIC S7 300/418 | Bool | 1 |  | 2 | 7
local | SIMATIC S7 300/419 | Bool | 1 |  | 3 | 0
remote | SIMATIC S7 300/420 | Bool | 1 |  | 3 | 1
SCADA | SIMATIC S7 300/421 | Bool | 1 |  | 3 | 2
test_local | SIMATIC S7 300/422 | Bool | 1 |  | 3 | 3
test_remote | SIMATIC S7 300/423 | Bool | 1 |  | 3 | 4
NM5 | SIMATIC S7 300/424 | Bool | 1 |  | 3 | 5
NM6 | SIMATIC S7 300/425 | Bool | 1 |  | 3 | 6
NM7 | SIMATIC S7 300/426 | Bool | 1 |  | 3 | 7
Time_set_b4_11_month | SIMATIC S7 300/427 | USInt | 1 |  | 4 | 0
Time_set_b4_11_year | SIMATIC S7 300/428 | USInt | 1 |  | 5 | 0
Time_set_b4_11_hour | SIMATIC S7 300/429 | USInt | 1 |  | 6 | 0
Time_set_b4_11_day | SIMATIC S7 300/430 | USInt | 1 |  | 7 | 0
Time_set_b4_11_second | SIMATIC S7 300/431 | USInt | 1 |  | 8 | 0
Time_set_b4_11_minute | SIMATIC S7 300/432 | USInt | 1 |  | 9 | 0
Time_set_b4_11_millisecondhigh_Byte | SIMATIC S7 300/433 | USInt | 1 |  | 10 | 0
Time_set_b4_11_millisecondlow_Byte | SIMATIC S7 300/434 | USInt | 1 |  | 11 | 0
_instr_No_1_b5 | SIMATIC S7 300/435 | USInt | 1 |  | 12 | 0
_instr_No_2_b6 | SIMATIC S7 300/436 | USInt | 1 |  | 13 | 0
_Data_val_1_b7 | SIMATIC S7 300/437 | USInt | 1 |  | 14 | 0
_Data_val_2_b8 | SIMATIC S7 300/438 | USInt | 1 |  | 15 | 0
Fil_FDR_FR_b14_15 | SIMATIC S7 300/439 | Real | 1 |  | 16 | 0
Fil_FDR_U1_b16_17 | SIMATIC S7 300/440 | Real | 1 |  | 20 | 0
Fil_FDR_U2_b18_19 | SIMATIC S7 300/441 | Real | 1 |  | 24 | 0
Fil_FDR_U3_b20_21 | SIMATIC S7 300/442 | Real | 1 |  | 28 | 0
Fil_FDR_U12_b22_23 | SIMATIC S7 300/443 | Real | 1 |  | 32 | 0
Fil_FDR_U13_b24_25 | SIMATIC S7 300/444 | Real | 1 |  | 36 | 0
Fil_FDR_U23_b26_27 | SIMATIC S7 300/445 | Real | 1 |  | 40 | 0
Fil_FDR_UAvr_b28_29 | SIMATIC S7 300/446 | Real | 1 |  | 44 | 0
Fil_BUS1_FR_b31_32 | SIMATIC S7 300/447 | Real | 1 |  | 48 | 0
Fil_BUS1_U1_b32_33 | SIMATIC S7 300/448 | Real | 1 |  | 52 | 0
Fil_BUS1_U2_b34_35 | SIMATIC S7 300/449 | Real | 1 |  | 56 | 0
Fil_BUS1_U3_b36_37 | SIMATIC S7 300/450 | Real | 1 |  | 60 | 0
Fil_BUS1_U12_b38_39 | SIMATIC S7 300/451 | Real | 1 |  | 64 | 0
Fil_BUS1_U13_b40_41 | SIMATIC S7 300/452 | Real | 1 |  | 68 | 0
Fil_BUS1_U23_b42_43 | SIMATIC S7 300/453 | Real | 1 |  | 72 | 0
Fil_BUS1_UAvr_b44_45 | SIMATIC S7 300/454 | Real | 1 |  | 76 | 0
Fil_BUS2_FR_b46_47 | SIMATIC S7 300/455 | Real | 1 |  | 80 | 0
Fil_BUS2_U1_b48_49 | SIMATIC S7 300/456 | Real | 1 |  | 84 | 0
Fil_BUS2_U2_b50_51 | SIMATIC S7 300/457 | Real | 1 |  | 88 | 0
Fil_BUS2_U3_b52_53 | SIMATIC S7 300/458 | Real | 1 |  | 92 | 0
Fil_BUS2_U12_b54_55 | SIMATIC S7 300/459 | Real | 1 |  | 96 | 0
Fil_BUS2_U13_b56_57 | SIMATIC S7 300/460 | Real | 1 |  | 100 | 0
Fil_BUS2_U23_b58_59 | SIMATIC S7 300/461 | Real | 1 |  | 104 | 0
Fil_BUS2_UAvr_b60_61 | SIMATIC S7 300/462 | Real | 1 |  | 108 | 0
Fil_FDR_I1_b62_63 | SIMATIC S7 300/463 | Real | 1 |  | 112 | 0
Fil_FDR_I2_b64_65 | SIMATIC S7 300/464 | Real | 1 |  | 116 | 0
Fil_FDR_I3_b65_67 | SIMATIC S7 300/465 | Real | 1 |  | 120 | 0
Fil_FDR_IAvr_b68_69 | SIMATIC S7 300/466 | Real | 1 |  | 124 | 0
Fil_FDR_P | SIMATIC S7 300/467 | Real | 1 |  | 128 | 0
Fil_FDR_Q | SIMATIC S7 300/468 | Real | 1 |  | 132 | 0
Fil_FDR_S | SIMATIC S7 300/469 | Real | 1 |  | 136 | 0
Fil_FDR_PF | SIMATIC S7 300/470 | Real | 1 |  | 140 | 0
Fil_FDR_PL1 | SIMATIC S7 300/471 | Real | 1 |  | 144 | 0
Fil_FDR_PL2 | SIMATIC S7 300/472 | Real | 1 |  | 148 | 0
Fil_FDR_PL3 | SIMATIC S7 300/473 | Real | 1 |  | 152 | 0
Fil_FDR_QL1 | SIMATIC S7 300/474 | Real | 1 |  | 156 | 0
Fil_FDR_QL2 | SIMATIC S7 300/475 | Real | 1 |  | 160 | 0
Fil_FDR_QL3 | SIMATIC S7 300/476 | Real | 1 |  | 164 | 0
Fil_FDR_PFL1 | SIMATIC S7 300/477 | Real | 1 |  | 168 | 0
Fil_FDR_PFL2 | SIMATIC S7 300/478 | Real | 1 |  | 172 | 0
Fil_FDR_PFL3 | SIMATIC S7 300/479 | Real | 1 |  | 176 | 0
Fc_FDR_FR_b14_15 | SIMATIC S7 300/480 | Real | 1 |  | 180 | 0
Fc_FDR_U1_b16_17 | SIMATIC S7 300/481 | Real | 1 |  | 184 | 0
Fc_FDR_U2_b18_19 | SIMATIC S7 300/482 | Real | 1 |  | 188 | 0
Fc_FDR_U3_b20_21 | SIMATIC S7 300/483 | Real | 1 |  | 192 | 0
Fc_FDR_U12_b22_23 | SIMATIC S7 300/484 | Real | 1 |  | 196 | 0
Fc_FDR_U13_b24_25 | SIMATIC S7 300/485 | Real | 1 |  | 200 | 0
Fc_FDR_U23_b26_27 | SIMATIC S7 300/486 | Real | 1 |  | 204 | 0
Fc_FDR_UAvr_b28_29 | SIMATIC S7 300/487 | Real | 1 |  | 208 | 0
Fact_BUS1_FR_b31_32 | SIMATIC S7 300/488 | Real | 1 |  | 212 | 0
Fact_BUS1_U1_b32_33 | SIMATIC S7 300/489 | Real | 1 |  | 216 | 0
Fact_BUS1_U2_b34_35 | SIMATIC S7 300/490 | Real | 1 |  | 220 | 0
Fact_BUS1_U3_b36_37 | SIMATIC S7 300/491 | Real | 1 |  | 224 | 0
Fact_BUS1_U12_b38_39 | SIMATIC S7 300/492 | Real | 1 |  | 228 | 0
Fact_BUS1_U13_b40_41 | SIMATIC S7 300/493 | Real | 1 |  | 232 | 0
Fact_BUS1_U23_b42_43 | SIMATIC S7 300/494 | Real | 1 |  | 236 | 0
Fact_BUS1_UAvr_b44_45 | SIMATIC S7 300/495 | Real | 1 |  | 240 | 0
Fc_BUS2_FR_b46_47 | SIMATIC S7 300/496 | Real | 1 |  | 244 | 0
Fc_BUS2_U1_b48_49 | SIMATIC S7 300/497 | Real | 1 |  | 248 | 0
Fc_BUS2_U2_b50_51 | SIMATIC S7 300/498 | Real | 1 |  | 252 | 0
Fc_BUS2_U3_b52_53 | SIMATIC S7 300/499 | Real | 1 |  | 256 | 0
Fc_BUS2_U12_b54_55 | SIMATIC S7 300/500 | Real | 1 |  | 260 | 0
Fc_BUS2_U13_b56_57 | SIMATIC S7 300/501 | Real | 1 |  | 264 | 0
Fc_BUS2_U23_b58_59 | SIMATIC S7 300/502 | Real | 1 |  | 268 | 0
Fc_BUS2_UAvr_b60_61 | SIMATIC S7 300/503 | Real | 1 |  | 272 | 0
Fc_FDR_I1_b62_63 | SIMATIC S7 300/504 | Real | 1 |  | 276 | 0
Fc_FDR_I2_b64_65 | SIMATIC S7 300/505 | Real | 1 |  | 280 | 0
Fc_FDR_I3_b65_67 | SIMATIC S7 300/506 | Real | 1 |  | 284 | 0
Fc_FDR_IAvr_b68_69 | SIMATIC S7 300/507 | Real | 1 |  | 288 | 0
Fc_FDR_P_b70_71 | SIMATIC S7 300/508 | Real | 1 |  | 292 | 0
Fc_FDR_Q_b72_73 | SIMATIC S7 300/509 | Real | 1 |  | 296 | 0
Fc_FDR_S_b74_75 | SIMATIC S7 300/510 | Real | 1 |  | 300 | 0
Fc_FDR_PF_b76_77 | SIMATIC S7 300/511 | Real | 1 |  | 304 | 0
Fc_FDR_PL1_b78_79 | SIMATIC S7 300/512 | Real | 1 |  | 308 | 0
Fc_FDR_PL2_b80_81 | SIMATIC S7 300/513 | Real | 1 |  | 312 | 0
Fc_FDR_PL3_b82_83 | SIMATIC S7 300/514 | Real | 1 |  | 316 | 0
Fc_FDR_QL1_b84_85 | SIMATIC S7 300/515 | Real | 1 |  | 320 | 0
Fc_FDR_QL2_b86_87 | SIMATIC S7 300/516 | Real | 1 |  | 324 | 0
Fc_FDR_QL3_b88_89 | SIMATIC S7 300/517 | Real | 1 |  | 328 | 0
Fc_FDR_PFL1_b90_91 | SIMATIC S7 300/518 | Real | 1 |  | 332 | 0
Fc_FDR_PFL2_b92_93 | SIMATIC S7 300/519 | Real | 1 |  | 336 | 0
Fc_FDR_PFL3_b94_95 | SIMATIC S7 300/520 | Real | 1 |  | 340 | 0
Fc_P_activ_b96_99 | SIMATIC S7 300/521 | Real | 1 |  | 344 | 0
Fc_P_obr_b100_103 | SIMATIC S7 300/522 | Real | 1 |  | 348 | 0
Fc_P_emk_reakt_b104_107 | SIMATIC S7 300/523 | Real | 1 |  | 352 | 0
Fc_P_ind_reakt_b108_111 | SIMATIC S7 300/524 | Real | 1 |  | 356 | 0
Fc_Io1_b112_113 | SIMATIC S7 300/525 | Real | 1 |  | 360 | 0
Fc_Uo1_b114_115 | SIMATIC S7 300/526 | Real | 1 |  | 364 | 0
Fc_Po1_b116_117 | SIMATIC S7 300/527 | Real | 1 |  | 368 | 0
Fc_Qo1_b118_119 | SIMATIC S7 300/528 | Real | 1 |  | 372 | 0
Fc_Alarm1_b120_121 | SIMATIC S7 300/529 | Real | 1 |  | 376 | 0
Fc_Alarm2_b122_123 | SIMATIC S7 300/530 | Real | 1 |  | 380 | 0
Fc_Alarm3_b124_125 | SIMATIC S7 300/531 | Real | 1 |  | 384 | 0
Fc_Alarm4_b126_127 | SIMATIC S7 300/532 | Real | 1 |  | 388 | 0
Fc_Alarm5_b128_129 | SIMATIC S7 300/533 | Real | 1 |  | 392 | 0
Fc_PM_Gen_number_b130_131 | SIMATIC S7 300/534 | Real | 1 |  | 396 | 0
Fc_PM_BCG_prstatus_b132_133 | SIMATIC S7 300/535 | Real | 1 |  | 400 | 0
Fc_PM_BCG_ownstatus_b134_135 | SIMATIC S7 300/536 | Real | 1 |  | 404 | 0
Fc_PM_BCG_netstatus_b136_137 | SIMATIC S7 300/537 | Real | 1 |  | 408 | 0
Fc_PM_8_9_b138_139 | SIMATIC S7 300/538 | Real | 1 |  | 412 | 0
Fc_PM_10_11_b140_141 | SIMATIC S7 300/539 | Real | 1 |  | 416 | 0
Fc_PM_12_13_b142_143 | SIMATIC S7 300/540 | Real | 1 |  | 420 | 0
Fc_PM_14_15_b144_145 | SIMATIC S7 300/541 | Real | 1 |  | 424 | 0
Fc_PM_16_17_b146_147 | SIMATIC S7 300/542 | Real | 1 |  | 428 | 0
Fc_PM_18_19_b148_149 | SIMATIC S7 300/543 | Real | 1 |  | 432 | 0
Fc_PM_20_21_b150_151 | SIMATIC S7 300/544 | Real | 1 |  | 436 | 0
Fc_PM_asym_load_point_b152_153 | SIMATIC S7 300/545 | Real | 1 |  | 440 | 0
Fc_PM_asym_power_factor_b151_155 | SIMATIC S7 300/546 | Real | 1 |  | 444 | 0
Fc_P_kw_b156_157 | SIMATIC S7 300/547 | Real | 1 |  | 448 | 0
Fc_P_ps_b158_159 | SIMATIC S7 300/548 | Real | 1 |  | 452 | 0
Fc_F_I_amp_b160_161 | SIMATIC S7 300/549 | Real | 1 |  | 456 | 0
Fc_F_I_ps_b162_163 | SIMATIC S7 300/550 | Real | 1 |  | 460 | 0
Fc_F_U_b164_165 | SIMATIC S7 300/551 | Real | 1 |  | 464 | 0
Fc_F_freg_b166_167 | SIMATIC S7 300/552 | Real | 1 |  | 468 | 0
Fc_F_cosf_b168_169 | SIMATIC S7 300/553 | Real | 1 |  | 472 | 0
Fc_B1_U_b170_171 | SIMATIC S7 300/554 | Real | 1 |  | 476 | 0
Fc_B1_freg1_b172_173 | SIMATIC S7 300/555 | Real | 1 |  | 480 | 0
Fc_RPM_b174_175 | SIMATIC S7 300/556 | Real | 1 |  | 484 | 0
Fc_BR1_ON_cycles_b176_177 | SIMATIC S7 300/557 | Real | 1 |  | 488 | 0
Fc_BR2_ON_cycles_b178_179 | SIMATIC S7 300/558 | Real | 1 |  | 492 | 0
Fc_BR3_ON_cycles_b180_181 | SIMATIC S7 300/559 | Real | 1 |  | 496 | 0
Fc_Start_counter_b182_183 | SIMATIC S7 300/560 | Real | 1 |  | 500 | 0
Fc_DP_MD33_R1_b184_185 | SIMATIC S7 300/561 | Real | 1 |  | 504 | 0
Fc_DP_MD33_R2_b186_187 | SIMATIC S7 300/562 | Real | 1 |  | 508 | 0
Fc_DP_MD33_R3_b188_189 | SIMATIC S7 300/563 | Real | 1 |  | 512 | 0
Kf_FDR_FR_b14_15 | SIMATIC S7 300/564 | Real | 1 |  | 516 | 0
Kf_FDR_U1_b16_17 | SIMATIC S7 300/565 | Real | 1 |  | 520 | 0
Kf_FDR_U2_b18_19 | SIMATIC S7 300/566 | Real | 1 |  | 524 | 0
Kf_FDR_U3_b20_21 | SIMATIC S7 300/567 | Real | 1 |  | 528 | 0
Kf_FDR_U12_b22_23 | SIMATIC S7 300/568 | Real | 1 |  | 532 | 0
Kf_FDR_U13_b24_25 | SIMATIC S7 300/569 | Real | 1 |  | 536 | 0
Kf_FDR_U23_b26_27 | SIMATIC S7 300/570 | Real | 1 |  | 540 | 0
Kf_FDR_UAvr_b28_29 | SIMATIC S7 300/571 | Real | 1 |  | 544 | 0
Kf_BUS1_FR_b31_32 | SIMATIC S7 300/572 | Real | 1 |  | 548 | 0
Kf_BUS1_U1_b32_33 | SIMATIC S7 300/573 | Real | 1 |  | 552 | 0
Kf_BUS1_U2_b34_35 | SIMATIC S7 300/574 | Real | 1 |  | 556 | 0
Kf_BUS1_U3_b36_37 | SIMATIC S7 300/575 | Real | 1 |  | 560 | 0
Kf_BUS1_U12_b38_39 | SIMATIC S7 300/576 | Real | 1 |  | 564 | 0
Kf_BUS1_U13_b40_41 | SIMATIC S7 300/577 | Real | 1 |  | 568 | 0
Kf_BUS1_U23_b42_43 | SIMATIC S7 300/578 | Real | 1 |  | 572 | 0
Kf_BUS1_UAvr_b44_45 | SIMATIC S7 300/579 | Real | 1 |  | 576 | 0
Kf_BUS2_FR_b46_47 | SIMATIC S7 300/580 | Real | 1 |  | 580 | 0
Kf_BUS2_U1_b48_49 | SIMATIC S7 300/581 | Real | 1 |  | 584 | 0
Kf_BUS2_U2_b50_51 | SIMATIC S7 300/582 | Real | 1 |  | 588 | 0
Kf_BUS2_U3_b52_53 | SIMATIC S7 300/583 | Real | 1 |  | 592 | 0
Kf_BUS2_U12_b54_55 | SIMATIC S7 300/584 | Real | 1 |  | 596 | 0
Kf_BUS2_U13_b56_57 | SIMATIC S7 300/585 | Real | 1 |  | 600 | 0
Kf_BUS2_U23_b58_59 | SIMATIC S7 300/586 | Real | 1 |  | 604 | 0
Kf_BUS2_UAvr_b60_61 | SIMATIC S7 300/587 | Real | 1 |  | 608 | 0
Kf_FDR_I1_b62_63 | SIMATIC S7 300/588 | Real | 1 |  | 612 | 0
Kf_FDR_I2_b64_65 | SIMATIC S7 300/589 | Real | 1 |  | 616 | 0
Kf_FDR_I3_b65_67 | SIMATIC S7 300/590 | Real | 1 |  | 620 | 0
Kf_FDR_IAvr_b68_69 | SIMATIC S7 300/591 | Real | 1 |  | 624 | 0
Kf_FDR_P_b70_71 | SIMATIC S7 300/592 | Real | 1 |  | 628 | 0
Kf_FDR_Q_b72_73 | SIMATIC S7 300/593 | Real | 1 |  | 632 | 0
Kf_FDR_S_b74_75 | SIMATIC S7 300/594 | Real | 1 |  | 636 | 0
Kf_FDR_PF_b76_77 | SIMATIC S7 300/595 | Real | 1 |  | 640 | 0
Kf_FDR_PL1_b78_79 | SIMATIC S7 300/596 | Real | 1 |  | 644 | 0
Kf_FDR_PL2_b80_81 | SIMATIC S7 300/597 | Real | 1 |  | 648 | 0
Kf_FDR_PL3_b82_83 | SIMATIC S7 300/598 | Real | 1 |  | 652 | 0
Kf_FDR_QL1_b84_85 | SIMATIC S7 300/599 | Real | 1 |  | 656 | 0
Kf_FDR_QL2_b86_87 | SIMATIC S7 300/600 | Real | 1 |  | 660 | 0
Kf_FDR_QL3_b88_89 | SIMATIC S7 300/601 | Real | 1 |  | 664 | 0
Kf_FDR_PFL1_b90_91 | SIMATIC S7 300/602 | Real | 1 |  | 668 | 0
Kf_FDR_PFL2_b92_93 | SIMATIC S7 300/603 | Real | 1 |  | 672 | 0
Kf_FDR_PFL3_b94_95 | SIMATIC S7 300/604 | Real | 1 |  | 676 | 0
Kf_P_activ_b96_99 | SIMATIC S7 300/605 | Real | 1 |  | 680 | 0
Kf_P_obr_b100_103 | SIMATIC S7 300/606 | Real | 1 |  | 684 | 0
Kf_P_emk_reakt_b104_107 | SIMATIC S7 300/607 | Real | 1 |  | 688 | 0
Kf_P_ind_reakt_b108_111 | SIMATIC S7 300/608 | Real | 1 |  | 692 | 0
Kf_Io1_b112_113 | SIMATIC S7 300/609 | Real | 1 |  | 696 | 0
Kf_Uo1_b114_115 | SIMATIC S7 300/610 | Real | 1 |  | 700 | 0
Kf_Po1_b116_117 | SIMATIC S7 300/611 | Real | 1 |  | 704 | 0
Kf_Qo1_b118_119 | SIMATIC S7 300/612 | Real | 1 |  | 708 | 0
Kf_Alarm1_b120_121 | SIMATIC S7 300/613 | Real | 1 |  | 712 | 0
Kf_Alarm2_b122_123 | SIMATIC S7 300/614 | Real | 1 |  | 716 | 0
Kf_Alarm3_b124_125 | SIMATIC S7 300/615 | Real | 1 |  | 720 | 0
Kf_Alarm4_b126_127 | SIMATIC S7 300/616 | Real | 1 |  | 724 | 0
Kf_Alarm5_b128_129 | SIMATIC S7 300/617 | Real | 1 |  | 728 | 0
Kf_PM_Gen_number_b130_131 | SIMATIC S7 300/618 | Real | 1 |  | 732 | 0
Kf_PM_BCG_prstatus_b132_133 | SIMATIC S7 300/619 | Real | 1 |  | 736 | 0
Kf_PM_BCG_ownstatus_b134_135 | SIMATIC S7 300/620 | Real | 1 |  | 740 | 0
Kf_PM_BCG_netstatus_b136_137 | SIMATIC S7 300/621 | Real | 1 |  | 744 | 0
Kf_PM_8_9_b138_139 | SIMATIC S7 300/622 | Real | 1 |  | 748 | 0
Kf_PM_10_11_b140_141 | SIMATIC S7 300/623 | Real | 1 |  | 752 | 0
Kf_PM_12_13_b142_143 | SIMATIC S7 300/624 | Real | 1 |  | 756 | 0
Kf_PM_14_15_b144_145 | SIMATIC S7 300/625 | Real | 1 |  | 760 | 0
Kf_PM_16_17_b146_147 | SIMATIC S7 300/626 | Real | 1 |  | 764 | 0
Kf_PM_18_19_b148_149 | SIMATIC S7 300/627 | Real | 1 |  | 768 | 0
Kf_PM_20_21_b150_151 | SIMATIC S7 300/628 | Real | 1 |  | 772 | 0
Kf_PM_asym_load_point_b152_153 | SIMATIC S7 300/629 | Real | 1 |  | 776 | 0
Kf_PM_asym_power_factor_b151_155 | SIMATIC S7 300/630 | Real | 1 |  | 780 | 0
Kf_P_kw_b156_157 | SIMATIC S7 300/631 | Real | 1 |  | 784 | 0
Kf_P_ps_b158_159 | SIMATIC S7 300/632 | Real | 1 |  | 788 | 0
Kf_F_I_amp_b160_161 | SIMATIC S7 300/633 | Real | 1 |  | 792 | 0
Kf_F_I_ps_b162_163 | SIMATIC S7 300/634 | Real | 1 |  | 796 | 0
Kf_F_U_b164_165 | SIMATIC S7 300/635 | Real | 1 |  | 800 | 0
Kf_F_freg_b166_167 | SIMATIC S7 300/636 | Real | 1 |  | 804 | 0
Kf_F_cosf_b168_169 | SIMATIC S7 300/637 | Real | 1 |  | 808 | 0
Kf_B1_U_b170_171 | SIMATIC S7 300/638 | Real | 1 |  | 812 | 0
Kf_B1_freg1_b172_173 | SIMATIC S7 300/639 | Real | 1 |  | 816 | 0
Kf_RPM_b174_175 | SIMATIC S7 300/640 | Real | 1 |  | 820 | 0
Kf_BR1_ON_cycles_b176_177 | SIMATIC S7 300/641 | Real | 1 |  | 824 | 0
Kf_BR2_ON_cycles_b178_179 | SIMATIC S7 300/642 | Real | 1 |  | 828 | 0
Kf_BR3_ON_cycles_b180_181 | SIMATIC S7 300/643 | Real | 1 |  | 832 | 0
Kf_Start_counter_b182_183 | SIMATIC S7 300/644 | Real | 1 |  | 836 | 0
Kf_DP_MD33_R1_b184_185 | SIMATIC S7 300/645 | Real | 1 |  | 840 | 0
Kf_DP_MD33_R2_b186_187 | SIMATIC S7 300/646 | Real | 1 |  | 844 | 0
Kf_DP_MD33_R3_b188_189 | SIMATIC S7 300/647 | Real | 1 |  | 848 | 0

## комент
Нужно создать UDT для WINCC?, автоматически она не создается. По структуре она должна повторять целевую UDT для PLC
1 | Перетаскиваем в таблицу тэгов данные из ДБ, в создании которого использовалась нужная UDT. Получаем одномерный массив с точной адресацией
2 | Экспортируем созданные тэги в эксель
3 | Для битов адресацию делаем руками с учетом соображений изложенных ниже
4 | Остальные данные встают нормально.
5 | Избавиться от длинных имен Read_write_Symap_Db_Devices_Wincc_Out_module_1_b0_11_Eventsbyte_350_365_b0_1_event_350
Для типов данных Real (Single), Int, Word: Поле Bit offset всегда должно быть равно 0, а значение Offset должно увеличиваться на физический размер переменной (Int = +2 байта, Real/Single = +4 байта).
Для типов данных Bool (Биты): Поле Offset показывает, в каком конкретно байте лежит бит, а поле Bit offset принимает значения строго от 0 до 7. Как только битов становится больше 8, Offset должен увеличиться на 1, а Bit offset снова сброситься в 0.
Если вы вставляете строки вручную, TIA Portal часто ошибается и начинает наращивать Bit offset дальше 7 (например, пишет 8, 9, 10...), либо перескакивает байты, из-за чего вся структура ниже "съезжает".
Чтобы офсеты и биты рассчитались идеально и автоматически без ручной правки, примените один секретный прием при вставке из Excel:
Обязательно замените в Excel слово Real на Single, а для битов используйте Bool.
3 | обрабатываем эксель (Убираем индексацию, добавляем "":; формула в этом документе). Формула ниже
4 | (="""" & A2 & """"&" : " & B2 & ";")
5 | копируем полученный столбец в блокнот.
6 | Из блокнота в визуал студио код в фойл создания UDT
7
8
9
10
11